## Slide 2
What Causes Thermal Runaway and What Are the Materials Processes Involved?
A foundational exploration of battery failure science, covering microscopic mechanisms, triggers, and safety implications for energy storage systems.
Instructors: Nathan B. Johnson, and Loraine Torres-Castro
SAND2026-21830C

## Slide 3
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 4: Learning Objectives
By the end of this tutorial, we will be able to:
Define what thermal runaway is and what its hazards are.
Identify which reactions contribute to thermal runaway.
Identity thermal runaway initiation methods.
Determine differences in hazards dependent on battery chemistry.
Critically assess claims of safety for new chemistries.
Determine thermal runaway hazards associated with system scale-up.

## Slide 5
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 6: Battery Storage Is Growing Fast — And the Safety Science Needs to Keep Up
Global Scaling
Grid-scale and distributed ESS are expanding rapidly worldwide.
Amplify Consequences
Larger deployments mean single-cell failures can have system-wide impacts.
Foundational Safety
Understanding cell-level science is not optional—it is the foundational requirement for every informed safety decision
Modern grid-scale ESS installations: Scaling brings new safety challenges.
https://www.energy-storage.news/moss-landing-worlds-biggest-battery-storage-project-is-now-3gwh-capacity/
https://eticaag.com/moss-landing-fire-lessons-for-bess-safety/

## Slide 7: Energy Storage Systems Face Several Hazard Types — Thermal Runaway Drives the Most Severe Outcomes
Electrical
Arc flash, short circuits, high-voltage DC risks.
Mechanical
Internal pressure, structural failure, vibrations.
Chemical
Electrolyte leaks, coolant exposure, toxicity.
Thermal
Thermal runaway: self-propagating.
Why is Thermal Runaway distinctive?
Self-Amplifying: Batteries contain both oxidant and reductant, making it uniquely difficult to interrupt.
Escalating Consequences: Can spread to neighboring cells (propagation), scaling with deployment size.
Diverse Hazards: Can produce fire, toxic gas, and overpressure simultaneously.

## Slide 8: Thermal Runaway Is a Self-Accelerating Process — Fire Is One Possible Outcome, Not the Definition
The Heat Balance Failure
A condition where a cell generates heat faster than it can release it to its surroundings - Accumulation.
Generation > Dissipation
Self-Reinforcing Cycle
Possible Outcomes
Venting & Gas Release
Swelling & Deformation
Fire & Combustion
Overpressure & Explosion
Toxic Vapor Cloud
*Outcomes depend on cell chemistry, state of charge, and environmental conditions.
STEP 1
Rising Temperature
STEP 2
Exothermic Reactions
STEP 3
More Heat Generated

## Slide 9
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 10: Cell Architecture: What We Are Working With
Control depends on maintaining the separation of reactive materials.
Energy storage is fundamentally the separation of highly reactive materials.
e-
charge
discharge
Anode (Negative)
Typically composed of graphite layers
Hosts lithium ions in charged state
High reactivity when SEI layer fails
Cathode (Positive)
Metal oxide or phosphate structures
Hosts lithium ions in discharged state
Can release oxygen at high heat
Separator
Porous plastic/ceramic membrane (~20μm)
Prevents physical contact (shorts circuit)
Melts/shrinks at 120–150°C
Electrolyte
Organic liquid solvent (carbon-based)
Facilitates ion flow between electrodes
Flammable under runaway conditions
Liu, C. et al. Mater. Today (2016) 19(2), 109-123

## Slide 11
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 12: The SEI: The Cell's Built-In But Fragile First Layer of Protection
Selective Membrane
Formed naturally on the anode; permits lithium ions while blocking electrolyte decomposition.
Thermal Sensitivity
Metastable layer; decomposition typically begins between ~80°C and 120°C.
Exothermic Breakdown
The process releases heat and exposes the reactive anode surface to the electrolyte.
Stage 1 of the Cascade
Often the triggering chemical event for cells with graphite anodes.
Normal Operation
SEI INTACT
REACTIVE
GRAPHITE ANODE
Interface is stable & protected
T > ~80-120°C
SEI DECOMPOSING
REACTIVE
GRAPHITE ANODE
Self-heating begins
Note: Thresholds are approximate and design-dependent

## Slide 13: When the Separator Fails, the Electrodes Make Contact — Releasing Stored Energy Rapidly
Material Breakdown
Polymer films (PE/PP) have defined melting points.
Heat causes the separator to shrink, melt, or fail.
Loss of physical barrier allows direct electrode contact.
Stored electrical energy converts to intense localized heat.
Stage: Intact Separator
Normal operation. Electrodes are physically isolated.
Threshold: Thermal Instability
Approximate and design-dependent temperature reach.
Event: Internal Short Circuit
Rapid electrical discharge. Cascade acceleration.
*Ceramic coatings can significantly alter these thresholds.

## Slide 14: At High Temperatures, Some Cathode Materials Release Oxygen — Which Can React With the Hot Electrolyte
*Relative comparisons only. Specific thresholds vary by design, state of charge, and heating rate.
Cathodes are lithium metal oxides; oxygen is part of their crystal structure.
Heat causes structural instability, releasing lattice oxygen as a gas.
Released oxygen drives highly exothermic reactions with the organic electrolyte.
Release severity depends heavily on the specific cathode chemistry.
NCA and NMC are more prone to combustion than LFP due to lower oxygen release thresholds.
Thermal Runaway Onset Temperature
Safer

## Slide 15: The Cascade of Material Breakdown
Thermal runaway is a sequential series of exothermic failures. Each stage releases heat that triggers the next, creating a self-sustaining feedback loop.
STAGE 1
SEI Decomposition
80°C – 120°C
STAGE 2
Separator Failure
120°C – 150°C
STAGE 3
Cathode Breakdown
150°C – 200°C+
STAGE 4
Full Combustion
Peak Runaway
Protective film breaks down
Exothermic heat release
Anode surface exposed
Plastic membrane melts/shrinks
Direct Anode-Cathode contact
Internal short circuit
Oxide structure collapses
Oxygen release occurs
Rapid heat acceleration
Electrolyte oxidation
Venting and pressure rise
Toxic gas & fire hazard
POINT OF NO RETURN: Typically reached during Stage 2/3 transition

## Slide 16
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 17: Thermal Abuse Triggers Internal Thermochemical Cascade
Exposing cells to temperatures beyond safe operating limits.
External heat initiates SEI decomposition, activating internal reactions.
Once internal reactions dominate, the cell becomes self-heating.
This is the primary mechanism for runaway propagation between cells.
COMMON EXTERNAL SOURCES
Nearby Fire
Cooling Failure
Neighboring Cell Runaway
Extreme Ambient Heat

## Slide 18: Thermal Ramp

## Slide 19: Electrical Abuse Triggers Chemical Instability and Structural Failure
Exceeding voltage limits forces materials into reactive states that bypass normal safety margins.
Over-discharge Risks
The Battery Management System (BMS) is a foundational safety component, not just a performance tool.
TUTORIAL PAGE 10
Overcharge Hazards
Excess Li forms reactive metallic layers on the anode surface.
Dendrites (metallic "needles“) can pierce the separator, causing internal shorts.
Over-delithiation lowers the oxygen release temperature threshold.
Overdischarge Hazards
Deep discharge causes the anode current collector to dissolve into electrolyte.
Dissolved copper redeposits during recharge, creating conductive bridges (copper dendrites).
Short circuit often triggers during subsequent charging cycles.

## Slide 20: Overcharge

## Slide 21: Nail Penetration

## Slide 22: Mechanical Deformation Triggers Instant Energy Release
Structural Collapse
Physical deformation—crushing, bending, or penetration—forces the anode and cathode into direct contact by destroying the separator.
Instant Internal Short Circuit
At high State of Charge (SOC), the stored chemical energy is converted to heat (Joule heating) almost instantaneously at the point of contact.
Localized Thermal Initiation
Intense localized heating can bypass early-stage instabilities (like SEI breakdown), triggering immediate cathode decomposition.
COMMON FAILURE SCENARIOS
Vehicular Accidents & Impacts
Improper Installation/Handling
Seismic or Structural Events
Manufacturing Defects
"Mechanical abuse is unique because it forces the cascade to jump directly to the most energetic stage."

## Slide 23: All Abuse Modes Converge into a Unified Internal Failure Cascade
Thermal Abuse
External heat drives internal temperature directly to the SEI decomposition threshold (~80°C).
Electrical Abuse
Overcharge/discharge causes lithium plating or copper dendrites, leading to internal shorts.
Mechanical Abuse
Physical crush or penetration collapses internal layers, causing instantaneous energy release.
The Unified Thermal Runaway Cascade
THE CONVERGENCE POINT
Self-Accelerating Heat Generation exceeds Dissipation
POINT OF NO RETURN
SHARED MATERIAL BREAKDOWN
SAFETY IMPLICATION
Regardless of the initiating event, the cell's internal chemistry dictates the final hazard severity. Mitigation must address the cascade itself."
SEI Layer Disintegration
Separator Melting & Massive Internal Short
Cathode Decomposition & Oxygen Release

## Slide 24
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 25: LFP Chemistry: Improved Stability is Not Total Immunity
Enhanced Stability (LFP)
Persistent Hazards
The phosphate bond holds oxygen more tightly than metal oxides.
Higher thermal onset temperatures for cathode decomposition.
Lower peak heat release rate during failure events.
Reduced tendency for self-sustained oxygen release.
Still contains flammable organic electrolyte solvents.
Stores significant chemical and electrical energy.
Can still vent, produce toxic or flammable gases, or ignite under abuse.
"More stable" does not equal "stable under all conditions."
Safety Assessment Reality Check
LFP reduces the likelihood of a self-sustained fire, but the hazard of toxic gas release and overpressure remains significant for indoor ESS installations.

## Slide 26: Beyond LFP: Every Chemistry Has a Profile
Balancing energy density with inherent thermal stability
NCA / High-Ni NMC
LFP (Lithium Iron Phosphate)
The Engineering Reality
• Highest energy density for long-range applications
• Lower structural stability at high temperatures
• Higher tendency for lattice oxygen release
• Exceptional thermal and structural stability
• Phosphate bonds hold oxygen tightly
• Tradeoff: Lower specific energy/density
"Safer" does not mean "immune." All chemistries require robust system-level management to mitigate thermal runaway risks.
NMC
NCA
LFP

## Slide 27: What About Sodium-Ion?
Lithium-ion and Sodium-ion have analogous materials
Lithium-ion
Sodium-ion
Cathodes:
Layered Metal Oxide (NMC, NCA)
Iron Phosphate (LFP)
Separator
Polypropylene
Polyethylene
Electrolyte
LiPF6
Carbonate and Ether Solvents
Anodes
Graphite
Silicon
Cathodes:
Layered Metal Oxide (NMF, NCO)
Iron Phosphate (NFPP)
Separator
Polypropylene
Polyethylene
Electrolyte
NaPF6
Carbonate and Ether Solvents
Anodes
Hard Carbon
Tin

## Slide 28: Sodium-Ion Has The Same Thermal Runaway Mechanism
50
100
150
200
250
300
350
400
450
>500
°C
SEI Decomposition
Electrolyte/Anode Reaction
Layered Metal Oxide Cathode Decomposition
Electrolyte Combustion
Separator Melting/Shrinking
Electrolyte Vaporization and Decomposition
Short Circuit
Binder Decomposition
Vent
Self-Heating
Thermal Runaway

## Slide 29: Scrutinizing Safety Claims: Beyond "Non-Flammable" Labels
Not all safety data is created equal—context and methodology are critical.
Scientific Caution: Be wary of absolute terms like "fireproof" or "intrinsically safe." Safety is a function of design, chemistry, and rigorous testing conditions.
Specific Testing Conditions
Evaluate the environment of the claim. Was the material tested in isolation or within a high-energy density environment?
Standardized Protocols
Claims must be backed by recognized industry standards (e.g., UL, IEC) rather than proprietary internal methods.
Full-Cell Performance
Verify that "stable" components do not introduce new failure modes (e.g., gas generation) when integrated into a complete cell.
Temperature ranges
Pressure variables
Repeatable metrics
Peer-reviewed data
System interaction
Real-world cycling

## Slide 30
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 31: Vented Gases Create Toxic and Explosive Risks Even Without Visible Fire
Venting Mechanism
Cell pressure rises until the vent or seal fails, releasing high-velocity gas and vapor.
Hidden Toxicity
Gases like HF are toxic and corrosive, posing immediate hazards to first responders.
Explosion Potential
H2 and CO can build up in enclosures and trigger delayed deflagrations if ignited.
Hydrogen Fluoride
H2
FLAMMABLE
Hydrogen
High buoyancy, wide explosive range
HF
HIGHLY TOXIC
Corrosive, penetrates skin, attacks bone.
Vapors
Flammable mist, contributes to fire spread.
ENVIRONMENTAL
CO
Asphyxiant, often produced in high volumes.
TOXIC & FLAMMABLE
Carbon Oxide
Critical Safety Insight
No flames does not mean the area is safe; gas hazards can persist, especially with poor ventilation.

## Slide 32: The Hazard Is Bigger Than the Flame
Thermal runaway produces multiple hazard domains requiring unique mitigation.
Safety design must address ALL domains: Suppression is not the same as gas management.
Fire
Visible combustion of electrolyte and gases. High radiant heat can drive propagation to neighboring cells.
Smoke & Particulates
Reduces visibility for responders and can leave conductive soot deposits on sensitive electronics.
Toxic & Flammable Gas
Venting can occur without fire. Gases may be toxic (HF, CO) or form explosive mixtures in enclosed spaces.
Overpressure
Rapid gas generation in sealed enclosures can cause structural failure or violent "projectiles" if not vented.

## Slide 33: Material Mitigation Strategies: Engineering Out the Risk
Advanced Separators
Ceramic Coatings: Prevents physical contact between electrodes at high temperatures.
Thermal Shutdown: Pores close automatically to stop ion flow when heat thresholds are reached.
Shrinkage Resistance: Maintains structural integrity up to ~200°C.
Stable Electrolytes
Flame Retardants: Organic phosphorous additives reduce the flammability of solvents.
SEI Stabilizers: Additives that create a more robust protective layer on the anode.
Non-Flammable Salts: Transitioning to salt systems with higher thermal decomposition points.
Cathode Engineering
Surface Coatings: Nanometer-thin metal oxide layers inhibit oxygen release.
Doping: Modifying the crystal structure to improve lattice stability during heating.
LFP Transition: Utilizing iron-phosphate chemistries for inherently lower oxygen release.

## Slide 34: From Cell Materials to ESS System Safety
Material-level insights drive robust engineering controls and system protections.
The Safety Bridge: We cannot engineer system safety without knowing the material thresholds of the cells inside. System-level protection is the final layer of defense for the cell's internal chemistry.
BMS Controls
Physical Spacing
Suppression
Prevents electrical abuse (overcharge)
Monitors thermal thresholds (SEI stability)
Acts as a primary safety component
Mitigates thermal abuse propagation
Prevents "domino effect" between cells
Engineered thermal isolation barriers
Manages the hazard domains (fire/gas)
Cools adjacent cells to stop cascade
Advanced detection of venting gases

## Slide 35
AGENDA
JUNE 2, 2026
Introduction to Thermal Runaway
Battery Components and Materials
Thermal Runaway Mechanism
Initiation Methods
Critical evaluation of “Safe” Chemistries
Scaling Up Safety
Closing Remarks

## Slide 36: Safety Starts with Science: Thermal Runaway Fundamentals
The Core Mechanism
Thermal runaway is a self-accelerating heat balance failure. It is a positive feedback loop where internal heat generation exceeds dissipation capacity.
The Material Cascade
Failure is a predictable sequence: SEI decomposition (80-120°C) → Separator failure → Cathode oxygen release → Electrolyte combustion.
Diverse Triggers, One Path
Thermal, Electrical, and Mechanical abuse modes differ in initiation but converge on the same internal exothermic chemical breakdown.
Material-to-System Safety
System resilience depends on cell chemistry (e.g., LFP vs Oxide) and engineering barriers to prevent cell-to-cell propagation.

## Slide 37: Poll Questions
Please visit Poll Everywhere via the QR code below (mobile) or at pe.app/essrf (laptop). If you would like to add your name, please update with the “pencil” icon. If not, feel free to remain anonymous

## Slide 38: Polling Questions
A cell can go into thermal runaway without catching fire.
  True
  False
Heat generation primarily comes from reaction between the cathode and the electrolyte (i.e. electrolyte combustion).
  True
  False
Which event initiates self-heating?
  Electrolyte reacting with the anode
  SEI decomposition
  Electrolyte decomposition
  Oxygen evolution from the cathode
Which cell chemistries are inherently safe?
  LFP
  Na-ion
  Non-flammable electrolytes
  All of the above
  None of the above
Which of the following is not a common thermal runaway initiation method?
  Optical
  Mechanical
  Electrical
  Thermal
Safety can be engineered at which level:
  Materials
  System
  Both a and b
  Neither a nor b

## Slide 39
THANK YOU
JUNE 2, 2026