## Test-2179
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2179
Scenario | 190V - 5kA Available - 21" fuse gap, calorimeter at 18"
Test Voltage (V) | 173.8
Arc Current (A) | 3140
Arc Voltage (V) | 71.11
Duration of Arc (s) | 0.005829
Arc Energy (kJ) | 0.9021 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.01 |  | Test 23-2179 was taken outside of the battery cabinet at the lowest voltage and lowest current. The voltage was achieved as per Test 23-2176, and the current was also achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at a higher voltage level.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21 |  |  | V | 192 | I | Vbat
Configuration | closed parallel |  |  | Ibf | 4800 | 0 | 192
|  |  |  | R | 0.04 | 1000 | 152
Time (s) | Current (A) | Voltage (V) |  |  |  | 2000 | 112
0.111 | 4509.9055 | 20.6246 |  |  |  | 3000 | 72
0.1112 | 4749.0894 | 20.6246 |  |  |  | 4000 | 32
0.1114 | 4908.5454 | 20.6246 |  |  |  | 4800 | 0
0.1116 | 4988.2734 | 20.6246
0.1118 | 5068.0014 | 20.6246
0.112 | 5147.7294 | 20.6276
0.1122 | 5147.7294 | 22.1726
0.1124 | 5068.0014 | 28.9121
0.1126 | 4908.5454 | 46.6502
0.1128 | 4589.6334 | 71.0478
0.113 | 4190.9935 | 95.0988
0.1132 | 3712.6255 | 113.1064
0.1134 | 3234.2575 | 125.8704
0.1136 | 2915.3456 | 135.7779
0.1138 | 2516.7056 | 150.4606
0.114 | 2277.5216 | 171.5368
0.1142 | 1878.8816 | 195.9402
0.1144 | 1480.2417 | 216.4326
0.1146 | 1081.6017 | 226.0224
0.1148 | 696.2025 | 225.5417

## Test-2180
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2180
Scenario | 240V - 5kA Available - 21" fuse gap, calorimeter at 18"
Test Voltage (V) | 271.7
Arc Current (A) | 3131
Arc Voltage (V) | 127.6
Duration of Arc (s) | 0.1917
Arc Energy (kJ) | 76.21 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.21 |  | Test 23-2180 was taken outside of the battery cabinet at intermediate voltage and lowest current. The voltage was achieved as per Test 23-2177, and the current was approximately achieved. A noticeable spark and smoke were observed. Furthermore, the exposed cables disconnected from their mounting, and the insulation block that contained the arc was burned. Review of high speed video shows the arc starting to expand towards behind the battery cabinet before growing towards the calorimeter placed in front of the battery cabinet. It then grows evenly to either side of the battery cabinet and is sustained. The arc is oriented downwards on both sides, briefly re-orients towards the ceiling on both sides, before finally extinguishing. It was decided to proceed with the next test at a lower voltage level.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.1093 | 1631.749 | 19.9249
0.1094 | 1404.539 | 22.0434
0.1095 | 1902.797 | 23.8042
0.1096 | 2611.533 | 25.5712
0.1097 | 2697.208 | 26.6951
0.1098 | 3265.348 | 28.2588 |  | V | 240 | I | Vbat
0.11 | 3717.783 | 33.6158 |  | Ibf | 5000 | 0 | 240
0.1103 | 3655.298 | 42.3232 |  | R | 0.048 | 1000 | 192
0.1105 | 4609.812 | 49.8992 |  |  |  | 2000 | 144
0.1108 | 4007.482 | 67.5542 |  |  |  | 3000 | 96
0.111 | 4231.599 | 83.5813 |  |  |  | 4000 | 48
0.1113 | 4423.077 | 110.82 |  |  |  | 5000 | 0
0.1115 | 4711.85 | 128.1223
0.1117 | 4415.295 | 137.4068
0.1118 | 4036.031 | 140.8411
0.1122 | 3656.766 | 150.2351
0.1123 | 3345.427 | 151.4175
0.1127 | 2995.24 | 147.9646
0.1133 | 2803.979 | 139.6577
0.114 | 3273.233 | 126.8676
0.115 | 3454.583 | 119.2605
0.116 | 3265.348 | 119.632
0.117 | 3580.739 | 121.1588
0.118 | 3549.2 | 119.8415
0.119 | 3328.426 | 119.7145
0.12 | 3675.357 | 120.4262
0.121 | 3486.122 | 118.197
0.122 | 3572.854 | 116.8775
0.123 | 3722.665 | 117.2946
0.124 | 3462.468 | 117.0781
0.125 | 3706.896 | 116.6617
0.126 | 3675.357 | 115.1896
0.127 | 3454.583 | 115.2169
0.128 | 3722.665 | 116.8293
0.129 | 3801.513 | 117.9354
0.13 | 3423.044 | 120.2983
0.131 | 3612.278 | 123.7763
0.132 | 3391.504 | 123.8628
0.133 | 3328.426 | 122.3919
0.134 | 3596.509 | 120.8899
0.135 | 3296.887 | 120.5768
0.136 | 3486.122 | 121.2941
0.137 | 3628.048 | 121.3114
0.138 | 3328.426 | 121.1064
0.139 | 3643.818 | 121.0347
0.14 | 3462.468 | 122.4961
0.141 | 3202.27 | 124.9496
0.142 | 3423.044 | 128.3766
0.143 | 3202.27 | 128.4596
0.144 | 3194.385 | 126.0832
0.145 | 3549.2 | 123.1536
0.146 | 3391.505 | 120.8069
0.147 | 3430.928 | 118.9293
0.148 | 3659.587 | 117.634
0.149 | 3407.274 | 117.1318
0.15 | 3675.357 | 119.182
0.151 | 3643.818 | 121.4903
0.152 | 3265.348 | 122.4549
0.153 | 3564.97 | 123.9642
0.154 | 3430.928 | 124.1733
0.155 | 3233.809 | 122.5448
0.156 | 3628.048 | 119.7389
0.157 | 3549.2 | 119.8435
0.158 | 3517.661 | 120.8302
0.159 | 3564.97 | 122.811
0.16 | 3391.505 | 123.1
0.161 | 3580.739 | 123.4119
0.162 | 3564.97 | 123.4754
0.163 | 3281.117 | 123.2468
0.164 | 3612.278 | 123.1138
0.165 | 3549.2 | 123.7027
0.166 | 3202.27 | 122.882
0.167 | 3517.661 | 122.3524
0.168 | 3517.661 | 123.9544
0.169 | 3233.809 | 126.0906
0.17 | 3470.352 | 127.0105
0.171 | 3359.965 | 125.5911
0.172 | 3423.044 | 126.5196
0.173 | 3438.813 | 127.773
0.174 | 3091.883 | 127.4563
0.175 | 3423.044 | 126.1758
0.176 | 3391.505 | 125.4055
0.177 | 3170.731 | 126.1901
0.178 | 3407.274 | 129.0467
0.179 | 3296.887 | 130.9279
0.18 | 3060.344 | 133.0735
0.181 | 3281.117 | 134.2354
0.182 | 3013.035 | 131.8536
0.183 | 3115.537 | 130.434
0.184 | 3296.887 | 130.3481
0.185 | 3076.113 | 128.9596
0.186 | 3241.694 | 129.9796
0.187 | 3328.426 | 132.8502
0.188 | 3044.574 | 131.7576
0.189 | 3281.117 | 127.7405
0.19 | 3486.122 | 124.0911
0.191 | 3139.191 | 125.0943
0.192 | 3438.813 | 128.5787
0.193 | 3210.154 | 129.0248
0.194 | 3233.809 | 128.2325
0.195 | 3454.583 | 129.2157
0.196 | 3210.154 | 131.4588
0.197 | 3178.615 | 133.2126
0.198 | 3265.348 | 131.0195
0.199 | 3076.113 | 127.8341
0.2 | 3359.965 | 126.0863
0.201 | 3359.965 | 126.3484
0.202 | 3107.652 | 127.5559
0.203 | 3391.505 | 131.5633
0.204 | 3241.694 | 134.3127
0.205 | 3052.459 | 132.7489
0.206 | 3344.196 | 131.7598
0.207 | 3139.191 | 131.8061
0.208 | 3202.27 | 133.0422
0.209 | 3218.039 | 134.0666
0.21 | 2965.726 | 132.2803
0.211 | 3202.27 | 133.0126
0.212 | 3265.348 | 134.6835
0.213 | 2949.957 | 135.9905
0.214 | 3139.191 | 137.3422
0.215 | 3107.652 | 136.0481
0.216 | 2918.418 | 135.0612
0.217 | 3154.961 | 135.1427
0.218 | 3139.191 | 134.1469
0.219 | 3107.652 | 134.44
0.22 | 3265.348 | 135.3262
0.221 | 3013.035 | 134.7793
0.222 | 3170.731 | 135.2473
0.223 | 3170.731 | 135.0057
0.224 | 2902.648 | 134.9459
0.225 | 3076.113 | 136.898
0.226 | 3076.113 | 136.9384
0.227 | 2855.339 | 136.946
0.228 | 3107.652 | 139.2661
0.229 | 3013.035 | 139.2959
0.23 | 2855.339 | 137.9863
0.231 | 3154.961 | 137.8096
0.232 | 2949.957 | 136.8538
0.233 | 3044.574 | 136.5114
0.234 | 3139.191 | 137.1246
0.235 | 3013.035 | 133.8013
0.236 | 3233.809 | 131.3986
0.237 | 3328.426 | 131.553
0.238 | 3076.113 | 131.0734
0.239 | 3281.117 | 132.1722
0.24 | 3328.426 | 135.6916
0.241 | 2855.339 | 137.8614
0.242 | 3091.883 | 136.1957
0.243 | 3076.113 | 132.6653
0.244 | 3170.731 | 135.1904
0.245 | 3218.039 | 138.0253
0.246 | 3107.652 | 137.3488
0.247 | 3020.92 | 138.3777
0.248 | 3107.652 | 138.8845
0.249 | 2776.491 | 138.8893
0.25 | 2981.496 | 138.5286
0.251 | 3060.344 | 137.5183
0.252 | 2823.8 | 137.012
0.253 | 3123.422 | 139.8653
0.254 | 3013.035 | 139.0499
0.255 | 2926.302 | 134.0893
0.256 | 3249.578 | 131.4782
0.257 | 3107.652 | 129.1768
0.258 | 3115.537 | 129.227
0.259 | 3344.196 | 131.5232
0.26 | 3044.574 | 130.9349
0.261 | 3265.348 | 133.9146
0.262 | 3296.887 | 138.8839
0.263 | 2823.8 | 141.1957
0.264 | 3076.113 | 142.2741
0.265 | 3013.035 | 140.9738
0.266 | 2729.183 | 140.0901
0.267 | 3013.035 | 141.2931
0.268 | 2855.339 | 140.2837
0.269 | 2831.685 | 139.3891
0.27 | 3123.422 | 141.259
0.271 | 2894.763 | 140.9347
0.272 | 2863.224 | 141.299
0.273 | 2997.265 | 141.9388
0.274 | 2744.952 | 140.317
0.275 | 2981.496 | 141.4686
0.276 | 3044.574 | 141.3919
0.277 | 2729.183 | 138.2621
0.278 | 3123.422 | 138.6475
0.279 | 3170.731 | 137.9446
0.28 | 2886.878 | 137.2546
0.281 | 3154.961 | 138.537
0.282 | 3076.113 | 139.5297
0.283 | 2886.878 | 142.1871
0.284 | 2997.265 | 142.1665
0.285 | 2776.491 | 141.3126
0.286 | 2886.878 | 150.001
0.287 | 2808.031 | 152.3944
0.288 | 2603.026 | 154.0496
0.289 | 2587.257 | 159.4963
0.29 | 2539.948 | 158.0941
0.2908 | 2309.481 | 157.6302
0.292 | 2571.487 | 157.7887
0.293 | 2461.1 | 155.2614
0.294 | 2476.87 | 154.8052
0.295 | 2713.413 | 155.7615
0.296 | 2453.215 | 156.7268
0.297 | 2500.524 | 157.8557
0.298 | 2603.026 | 154.456
0.299 | 2413.791 | 155.2578
0.3 | 2445.331 | 167.9936
0.301 | 2161.478 | 181.7131
0.3017 | 1650.775 | 194.3268
0.303 | 1404.539 | 216.2938
0.3038 | 1044.66 | 231.6675
0.304 | 710.678 | 236.0768
0.3043 | 474.135 | 242.4082
0.305 | 190.283 | 254.2984
0.306 | 95.666 | 249.3192

## Test-2181
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2181
Scenario | 192V - 5kA Available - calorimeter at 18, Using simulated breaker , arc in open air
Test Voltage (V) | 173.8
Arc Current (A) | 2482
Arc Voltage (V) | 163.7
Duration of Arc (s) | 0.00194
Arc Energy (kJ) | 0.5903 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.02 |  | Test 23-2181 was taken outside of the battery cabinet at the lowest voltage and lowest current. The voltage was achieved as per Test 23-2176, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at the same voltage level
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.1095 | 1838.3502 | 10.389
0.1096 | 2611.533 | 11.5567
0.1099 | 2816.4191 | 15.3571 |  | I | Vbat
0.11 | 3207.0644 | 16.0932 |  | 0 | 192
0.1103 | 3655.2983 | 18.3017 |  | 5000 | 0
0.1105 | 3783.3652 | 19.8315
0.1108 | 4007.4821 | 22.5597
0.111 | 4231.599 | 25.4228
0.1113 | 4423.0769 | 26.8225
0.1115 | 4711.8496 | 33.8835
0.112 | 4567.7745 | 75.3305
0.1125 | 3639.1239 | 122.0245
0.1127 | 2912.4692 | 149.1788
0.113 | 1918.1773 | 176.3902
0.1132 | 1202.7979 | 204.7944
0.1135 | 661.7363 | 241.925

## Test-2182
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2182
Scenario | 192V - 5kA Available - calorimeter at 18" Using simulated breaker , arc in open air
Test Voltage (V) | 173.8
Arc Current (A) | 2241
Arc Voltage (V) | 140.4
Duration of Arc (s) | 0.004554
Arc Energy (kJ) | 1.107 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.08 |  | Test 23-2182 was taken outside of the battery cabinet at the lowest voltage and lowest current. The voltage was achieved as per Test 23-2176, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at a higher voltage level.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.111 | 3938.369 | 8.659
0.112 | 4890.145 | 12.241
0.113 | 3592.318 | 19.391
0.114 | 2390.026 | 107.054
0.116 | 951.123 | 160.465
0.117 | 173.577 | 193.024
0.119 | 28.079 | 203.876
|  |  |  | I | Vbat
|  |  |  | 0 | 192
|  |  |  | 5000 | 0

## Test-2183
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2183
Scenario | 240V - 5kA Available - calorimeter at 18" Using simulated breaker , arc in open air
Test Voltage (V) | 271.7
Arc Current (A) | 2300
Arc Voltage (V) | 159.7
Duration of Arc (s) | 0.2568
Arc Energy (kJ) | 92.32 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 1.91 |  | Test 23-2183 was taken outside of the battery cabinet at intermediate voltage and lowest current. The voltage was achieved as per Test 23-2177, and the current was approximately achieved. A noticeable spark and smoke were observed, leading to a small flame on the insulation block that contained the arc. As a result, the insulated cables were burned at end that was fused. Review of high-speed video shows the arc grow substantially towards the calorimeter placed in front of the battery cabinet. It is then sustained in that manner, before extinguishing. It was decided to proceed with the next test at the same voltage level.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.112 | 4567.278 | 78.446
0.115 | 3148.911 | 138.224
0.118 | 2873.785 | 142.052
0.121 | 2812.349 | 145.356
0.124 | 2684.134 | 144.835
0.127 | 2916.523 | 140.818
0.13 | 2860.429 | 141.982
0.133 | 2956.59 | 140.554
0.136 | 2844.403 | 144.625 |  | I | Vbat
0.139 | 2804.336 | 146.667 |  | 0 | 240
0.142 | 2876.456 | 146.339 |  | 5000 | 0
0.145 | 2828.376 | 148.888
0.148 | 2764.269 | 148.985
0.151 | 2716.189 | 148.801
0.154 | 2684.134 | 150.381
0.157 | 2636.055 | 151.305
0.16 | 2531.881 | 151.616
0.163 | 2571.948 | 151.506
0.166 | 2563.934 | 151.235
0.169 | 2531.881 | 151.217
0.172 | 2620.028 | 151.445
0.175 | 2628.041 | 151.383
0.178 | 2684.135 | 149.375
0.181 | 2732.215 | 151.48
0.184 | 2612.014 | 154.338
0.187 | 2587.975 | 155.38
0.19 | 2531.881 | 156.428
0.193 | 2459.76 | 157.477
0.196 | 2403.667 | 158.812
0.199 | 2363.6 | 158.862
0.202 | 2339.56 | 159.265
0.205 | 2347.573 | 160.943
0.208 | 2355.587 | 161.598
0.211 | 2323.533 | 163.148
0.214 | 2299.493 | 164.437
0.217 | 2499.827 | 164.071
0.22 | 2443.734 | 163.884
0.223 | 2307.506 | 163.081
0.226 | 2531.881 | 161.268
0.229 | 2403.667 | 163.228
0.232 | 2131.212 | 167.908
0.235 | 2115.185 | 167.814
0.238 | 2107.171 | 168.816
0.241 | 2203.333 | 164.218
0.244 | 2115.185 | 167.991
0.247 | 2275.453 | 168.836
0.25 | 1962.931 | 173.704
0.253 | 2339.56 | 169.403
0.256 | 2131.212 | 172.572
0.259 | 2027.038 | 174.441
0.262 | 2211.346 | 174.197
0.265 | 1954.918 | 173.684
0.268 | 2051.078 | 171.737
0.271 | 2059.092 | 172.943
0.274 | 2083.132 | 166.979
0.277 | 2179.292 | 167.788
0.28 | 1970.944 | 174.453
0.283 | 1898.824 | 175.968
0.286 | 2107.172 | 171.791
0.289 | 2115.185 | 169.574
0.292 | 2275.453 | 166.81
0.295 | 2259.426 | 168.224
0.298 | 2147.239 | 171.428
0.301 | 2019.025 | 173.007
0.304 | 2123.199 | 172.659
0.307 | 1922.864 | 173.43
0.31 | 1970.944 | 172.451
0.313 | 1898.824 | 176.286
0.316 | 1890.811 | 179.661
0.319 | 1802.664 | 179.352
0.322 | 2051.079 | 171.657
0.325 | 2131.212 | 171.994
0.328 | 2027.038 | 178.066
0.331 | 1898.824 | 178.895
0.334 | 2051.078 | 171.501
0.337 | 2099.159 | 174.379
0.34 | 2019.025 | 175.273
0.343 | 2099.159 | 172.643
0.346 | 2027.038 | 178.433
0.349 | 1762.597 | 179.574
0.352 | 1922.864 | 176.777
0.355 | 1794.65 | 179.941
0.358 | 1818.691 | 180.572
0.361 | 1922.865 | 177.46
0.364 | 1922.864 | 177.927
0.367 | 2195.319 | 166.286
0.37 | 2155.252 | 184.966
0.376 | 572.611 | 241.316

## Test-2184
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2184
Scenario | 240V - 5kA Available - A: calorimeter at 18", B: calorimeter at 6" Using simulated breaker , arc in open air
Test Voltage (V) | 271.7
Arc Current (A) | 2648
Arc Voltage (V) | 154.9
Duration of Arc (s) | 0.01685
Arc Energy (kJ) | 6.643 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.08 |  | Test 23-2184 was taken outside of the battery cabinet at intermediate voltage and lowest current. The voltage was achieved as per Test 23-2177, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at the same voltage level.
Incident Energy at 6" distance (cal/cm²) | 0.18
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.113 | 4330.649 | 99.326
0.114 | 3634.417 | 121.766
0.115 | 3215.065 | 135.651
0.116 | 2935.497 | 138.902
0.117 | 2733.886 | 141.988
0.118 | 2822.595 | 141.952
0.119 | 2685.499 | 141.848
0.12 | 2927.433 | 140.463
0.121 | 2895.175 | 140.738 |  | I | Vbat
0.122 | 2774.208 | 140.985 |  | 0 | 240
0.123 | 2879.046 | 143.768 |  | 5000 | 0
0.124 | 2806.466 | 146.537
0.125 | 2500.016 | 153.194
0.126 | 2451.63 | 161.813
0.127 | 2161.308 | 170.463
0.128 | 1758.085 | 195.397
0.129 | 1280.669 | 224.8
0.13 | 129.064 | 240.334

## Test-2185
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2185
Scenario | 240V - 5kA Available - A: calorimeter at 18", B: calorimeter at 6" Using simulated breaker , arc in open air
Test Voltage (V) | 271.7
Arc Current (A) | 2375
Arc Voltage (V) | 172.2
Duration of Arc (s) | 0.008397
Arc Energy (kJ) | 3.137 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.03 |  | Test 23-2185 was taken outside of the battery cabinet at intermediate voltage and lowest current. The voltage was achieved as per Test 23-2177, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at a higher voltage level.
Incident Energy at 6" distance (cal/cm²) | 0.09
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.111 | 5158.811 | 46.729
0.112 | 5624.262 | 96.281
0.113 | 4308.255 | 125.982
0.114 | 3393.976 | 142.082
0.115 | 3200.039 | 145.081
0.116 | 2957.616 | 147.194
0.117 | 2739.436 | 165.224
0.118 | 2367.722 | 182.089 |  | I | Vbat
0.119 | 2012.17 | 210.244 |  | 0 | 240
0.12 | 963.693 | 243.106 |  | 5000 | 0
0.121 | 436.425 | 251.522

## Test-2186
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2186
Scenario | 480V - 5kA Available - A: calorimeter at 18", B: calorimeter at 6" Using simulated breaker , arc in open air
Test Voltage (V) | 434.9
Arc Current (A) | 3496
Arc Voltage (V) | 156.6
Duration of Arc (s) | 0.1448
Arc Energy (kJ) | 79.21 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.74 |  | Test 23-2186 was taken outside of the battery cabinet at the highest voltage and lowest current. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A noticeable spark and smoke were observed, leading to a small flame on the insulation block that contained the arc. As a result, the insulated cables were burned at the end that was fused. Review of high-speed video shows the arc grows towards the calorimeter placed in front of the battery cabinet, as well as away from the calorimeter towards the back-side of the battery cabinet. It then grows towards the ceiling and floor, before extinguishing. It was decided to proceed with the next test at the same voltage level.
Incident Energy at 6" distance (cal/cm²) | 3.71
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21
Configuration | closed parallel
Time (s) | Current (A) | Voltage (V)
0.11 | 2187.426 | 20.434
0.111 | 4600.307 | 22.034
0.112 | 5123.336 | 39.503
0.113 | 4112.1 | 102.324
0.114 | 3766.127 | 122.926
0.115 | 3934.632 | 127.319
0.116 | 3578.021 | 132.639
0.117 | 3744.44 | 138.57
0.118 | 3673.117 | 141.241 |  | V | 480 | I | Vbat
0.119 | 3482.925 | 142.659 |  | Ibf | 5000 | 0 | 480
0.12 | 3815.762 | 142.98 |  | R | 0.096 | 1000 | 384
0.121 | 3649.343 | 141.394 |  |  |  | 2000 | 288
0.122 | 3530.473 | 141.254 |  |  |  | 3000 | 192
0.123 | 3815.762 | 141.843 |  |  |  | 4000 | 96
0.124 | 3506.699 | 140.359 |  |  |  | 5000 | 0
0.125 | 3720.666 | 139.151
0.126 | 3768.214 | 139.008
0.127 | 3530.473 | 138.685
0.128 | 3791.988 | 141.53
0.129 | 3744.44 | 142.74
0.13 | 3482.925 | 142.99
0.131 | 3791.988 | 144.259
0.132 | 3625.569 | 143.026
0.133 | 3435.377 | 144.75
0.134 | 3744.44 | 147.798
0.135 | 3554.247 | 147.427
0.136 | 3768.214 | 148.827
0.137 | 3768.214 | 149.146
0.138 | 3506.699 | 147.491
0.139 | 3625.569 | 149.912
0.14 | 3696.892 | 150.329
0.141 | 3364.054 | 148.654
0.142 | 3649.343 | 150.093
0.143 | 3601.795 | 150.621
0.144 | 3411.603 | 150.85
0.145 | 3744.44 | 152.073
0.146 | 3578.021 | 151.353
0.147 | 3482.925 | 152.341
0.148 | 3744.44 | 153.907
0.149 | 3387.829 | 152.841
0.15 | 3625.569 | 153.887
0.151 | 3649.343 | 155.121
0.152 | 3364.054 | 154.574
0.153 | 3601.795 | 155.458
0.154 | 3578.021 | 155.318
0.155 | 3364.054 | 154.774
0.156 | 3649.343 | 155.666
0.157 | 3482.925 | 155.046
0.158 | 3316.506 | 155.222
0.159 | 3649.343 | 155.943
0.16 | 3411.603 | 155.072
0.161 | 3482.925 | 156.214
0.162 | 3673.117 | 156.593
0.163 | 3411.603 | 155.49
0.164 | 3673.117 | 157.326
0.165 | 3601.795 | 157.685
0.166 | 3292.732 | 157.082
0.167 | 3578.021 | 158.393
0.168 | 3506.699 | 157.597
0.169 | 3340.28 | 157.134
0.17 | 3696.892 | 158.701
0.171 | 3482.925 | 158.664
0.172 | 3435.377 | 159.793
0.173 | 3649.343 | 160.053
0.174 | 3364.054 | 158.042
0.175 | 3625.569 | 158.892
0.176 | 3578.021 | 160.408
0.177 | 3292.732 | 160.931
0.178 | 3554.247 | 162.651
0.179 | 3554.247 | 162.696
0.18 | 3292.732 | 161.281
0.181 | 3625.569 | 161.837
0.182 | 3435.377 | 161.246
0.183 | 3268.958 | 161.147
0.184 | 3601.795 | 162.717
0.185 | 3316.506 | 161.694
0.186 | 3435.377 | 163.327
0.187 | 3601.795 | 164.764
0.188 | 3292.732 | 163.853
0.189 | 3482.925 | 164.437
0.19 | 3506.699 | 160.733
0.191 | 3245.184 | 157.298
0.192 | 3530.473 | 158.139
0.193 | 3482.925 | 157.305
0.194 | 3340.28 | 158.446
0.195 | 3649.343 | 162.489
0.196 | 3411.603 | 159.828
0.197 | 3387.829 | 158.751
0.198 | 3625.569 | 159.828
0.199 | 3364.054 | 158.226
0.2 | 3387.829 | 162.16
0.201 | 3530.473 | 161.658
0.202 | 3316.506 | 156.675
0.203 | 3673.117 | 158.338
0.204 | 3554.247 | 161.428
0.205 | 3292.732 | 160.697
0.206 | 3649.343 | 159.571
0.207 | 3459.151 | 157.568
0.208 | 3292.732 | 158.18
0.209 | 3625.569 | 159.368
0.21 | 3411.603 | 157.214
0.211 | 3673.117 | 159.278
0.212 | 3625.569 | 160.943
0.213 | 3387.829 | 158.452
0.214 | 3578.021 | 158.601
0.215 | 3601.795 | 159.551
0.216 | 3245.184 | 159.226
0.217 | 3578.021 | 161.406
0.218 | 3482.925 | 160.647
0.219 | 3364.054 | 159.988
0.22 | 3649.343 | 161.428
0.221 | 3411.603 | 158.441
0.222 | 3435.377 | 158.486
0.223 | 3649.343 | 160.234
0.224 | 3316.506 | 158.597
0.225 | 3578.021 | 162.539
0.226 | 3530.473 | 167.036
0.227 | 3221.41 | 163.9
0.228 | 3554.247 | 162.135
0.229 | 3459.151 | 163.728
0.23 | 3268.958 | 162.835
0.231 | 3578.021 | 162.705
0.232 | 3387.829 | 162.957
0.233 | 3268.958 | 163.775
0.234 | 3578.021 | 163.601
0.235 | 3316.506 | 163.129
0.236 | 3387.829 | 164.914
0.237 | 3554.247 | 164.739
0.238 | 3292.732 | 163.825
0.239 | 3435.377 | 166.002
0.24 | 3435.377 | 166.766
0.241 | 3150.088 | 165.17
0.242 | 3530.473 | 165.608
0.243 | 3411.603 | 165.54
0.244 | 3268.958 | 166.353
0.245 | 3601.795 | 168.478
0.246 | 3364.054 | 167.576
0.247 | 3387.829 | 168.672
0.248 | 3530.473 | 169.25
0.249 | 3245.184 | 167.761
0.25 | 3530.473 | 168.133
0.251 | 3459.151 | 172.117
0.252 | 3126.314 | 177.207
0.253 | 3411.603 | 179.556
0.254 | 3364.054 | 176.601
0.255 | 3197.636 | 172.045
0.256 | 3506.699 | 167.927
0.257 | 3411.603 | 161.874
0.258 | 3482.925 | 160.383
0.259 | 3601.795 | 167.554
0.26 | 3197.636 | 175.023
0.261 | 3435.377 | 179.95
0.262 | 3411.603 | 184.952
0.263 | 3054.991 | 184.568
0.264 | 3292.732 | 180.976
0.265 | 3435.377 | 184.549
0.266 | 2936.121 | 188.954
0.267 | 3245.184 | 190.213
0.268 | 3078.765 | 190.696
0.269 | 3007.443 | 194.504
0.27 | 3268.958 | 200.251
0.271 | 2959.895 | 203.336
0.272 | 2912.347 | 206.062
0.273 | 3126.314 | 205.024
0.274 | 2841.025 | 205.341
0.275 | 2912.347 | 211.034
0.276 | 2983.669 | 215.721
0.277 | 2674.606 | 222.643
0.278 | 2936.121 | 230.495
0.279 | 2745.928 | 229.412
0.28 | 2627.058 | 230.597
0.281 | 2817.251 | 242.544
0.282 | 2531.962 | 252.817
0.283 | 2222.899 | 272.455
0.284 | 2508.188 | 257.28
0.285 | 2413.091 | 240.983
0.286 | 2722.154 | 238.923
0.287 | 2769.702 | 236.977
0.288 | 2531.962 | 234.136
0.289 | 2793.477 | 232.285
0.29 | 2793.477 | 228.68
0.291 | 2555.736 | 227.656
0.292 | 2841.025 | 234.841
0.293 | 2627.058 | 236.593
0.294 | 2627.058 | 233.308
0.295 | 2888.573 | 225.947
0.296 | 2769.702 | 212.729
0.297 | 2841.025 | 219.901
0.298 | 2959.895 | 223.736
0.299 | 2579.51 | 227.287
0.3 | 2912.347 | 222.854
0.301 | 3007.443 | 209.187
0.302 | 2674.606 | 226.935
0.303 | 2769.702 | 248.53
0.304 | 2627.058 | 254.98
0.305 | 2341.769 | 256.362
0.306 | 2603.284 | 268.472
0.307 | 2151.576 | 276.676
0.308 | 2294.221 | 264.376
0.309 | 2722.154 | 231.328
0.31 | 2389.318 | 260.118
0.311 | 2389.317 | 279.465
0.312 | 2115.916 | 311.517
0.313 | 1676.095 | 314.179
0.314 | 2104.028 | 311.851
0.315 | 1806.853 | 327.76
0.316 | 1771.191 | 313.199
0.317 | 2032.706 | 312.155
0.318 | 1913.836 | 324.578
0.319 | 1557.224 | 343.708
0.32 | 1676.095 | 339.099
0.321 | 1533.45 | 329.132
0.322 | 1747.417 | 325.922
0.323 | 2008.932 | 276.06
0.324 | 2222.899 | 244.554
0.325 | 2317.995 | 308.66
0.326 | 1723.643 | 324.429
0.327 | 1818.739 | 288.606
0.328 | 2222.899 | 289.923
0.329 | 2270.447 | 295.725
0.33 | 1382.881 | 378.868
0.331 | 844.002 | 403.801
0.332 | 915.324 | 396.125
0.333 | 701.358 | 444.178
0.334 | 844.002 | 396.649
0.335 | 1200.613 | 374.112
0.336 | 1069.856 | 411.231
0.337 | 701.358 | 376.786
0.338 | 1176.839 | 368.244
0.339 | 1081.743 | 397.555
0.34 | 808.341 | 414.28
0.341 | 760.793 | 412.632
0.342 | 915.324 | 388.508
0.343 | 1153.065 | 356.992
0.344 | 1176.839 | 395.428
0.345 | 1034.195 | 414.154
0.346 | 653.809 | 423.506
0.347 | 511.165 | 435.4
0.348 | 939.098 | 399.151
0.349 | 511.165 | 452.923
0.35 | 273.424 | 490.227

## Test-2187
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2187
Scenario | 480V - 5kA Available - A: calorimeter at 18", B: calorimeter at 6" Using simulated breaker , arc in open air
Test Voltage (V) | 434.9
Arc Current (A) | 3462
Arc Voltage (V) | 158
Duration of Arc (s) | 0.1803
Arc Energy (kJ) | 97.47 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.33 |  | Test 23-2187 was taken outside of the battery cabinet at the highest voltage and lowest current. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A noticeable spark and smoke were observed, leading to a small flame on the insulation block that contained the arc. As a result, the insulated cables were burned at the ends that were fused. Review of high-speed video shows the arc grows towards just above the calorimeter placed in front of the battery cabinet, as well as away from the calorimeter towards the back-side of the battery cabinet. It is then sustained in this manner, before extinguishing. It was decided to proceed with the next test at a higher current level.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 2.67
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 2487.229 | 13.297 |  |  |  | 0.11 | 2820.959 | 11.085
0.111 | 4770.778 | 14.871 |  |  |  | 0.111 | 4702.698 | 13.807
0.112 | 5213.528 | 34.485 |  |  |  | 0.112 | 5254.033 | 44.703
0.113 | 4508.467 | 99.382 |  |  |  | 0.113 | 4420.641 | 82.836
0.114 | 3963.647 | 122.727 |  |  |  | 0.114 | 3879.079 | 117.309
0.115 | 3933.35 | 125.853 |  |  |  | 0.115 | 4030.954 | 122.184
0.116 | 3627.141 | 126.081 |  |  |  | 0.116 | 3720.571 | 121.922
0.117 | 3915.575 | 126.039 |  |  |  | 0.117 | 3997.263 | 121.964
0.118 | 3915.575 | 126.737 |  |  |  | 0.118 | 3863.219 | 122.779
0.119 | 3699.249 | 128.571 |  |  |  | 0.119 | 3720.571 | 124.532
0.12 | 4011.72 | 131.776 |  |  |  | 0.12 | 3934.542 | 127.856
0.121 | 3819.43 | 134.121 |  |  |  | 0.121 | 3827.557 | 129.166
0.122 | 3699.249 | 135.558 |  |  |  | 0.122 | 3702.74 | 130.646
0.123 | 3939.611 | 137.162 |  |  |  | 0.123 | 3863.219 | 133.017
0.124 | 3651.177 | 138.342 |  |  |  | 0.124 | 3667.078 | 134.17
0.125 | 3795.394 | 140.063 |  |  |  | 0.125 | 3522.46 | 135.928
0.126 | 3843.466 | 141.772 |  |  |  | 0.126 | 3791.895 | 137.424
0.127 | 3579.069 | 141.793 |  |  |  | 0.127 | 3595.754 | 137.527
0.128 | 3795.394 | 143.323 |  |  |  | 0.128 | 3842.071 | 138.626
0.129 | 3819.43 | 143.684 |  |  |  | 0.129 | 3786.608 | 138.607
0.13 | 3555.032 | 142.178 |  |  |  | 0.13 | 3577.923 | 137.835
0.131 | 3843.466 | 143.294 |  |  |  | 0.131 | 3847.358 | 138.797
0.132 | 3723.286 | 142.954 |  |  |  | 0.132 | 3684.909 | 138.386
0.133 | 3434.852 | 140.96 |  |  |  | 0.133 | 3542.262 | 136.814
0.134 | 3867.503 | 140.125 |  |  |  | 0.134 | 3791.895 | 135.797
0.135 | 3675.213 | 140.362 |  |  |  | 0.135 | 3667.078 | 136.607
0.136 | 3843.466 | 143.5 |  |  |  | 0.136 | 3631.416 | 140.219
0.137 | 3843.466 | 148.454 |  |  |  | 0.137 | 3738.402 | 144.751
0.138 | 3530.996 | 149.636 |  |  |  | 0.138 | 3542.262 | 146.03
0.139 | 3651.177 | 149.855 |  |  |  | 0.139 | 3595.754 | 146.119
0.14 | 3723.286 | 150.038 |  |  |  | 0.14 | 3649.247 | 146.13
0.141 | 3434.852 | 150.345 |  |  |  | 0.141 | 3453.107 | 146.331
0.142 | 3675.213 | 152.572 |  |  |  | 0.142 | 3663.762 | 148.566
0.143 | 3627.141 | 152.386 |  |  |  | 0.143 | 3577.923 | 148.492
0.144 | 3410.815 | 150.277 |  |  |  | 0.144 | 3506.6 | 146.603
0.145 | 3819.43 | 151.108 |  |  |  | 0.145 | 3745.659 | 146.604
0.146 | 3627.141 | 150.381 |  |  |  | 0.146 | 3613.585 | 146.303
0.147 | 3482.924 | 150.669 |  |  |  | 0.147 | 3524.431 | 146.342
0.148 | 3771.358 | 151.434 |  |  |  | 0.148 | 3702.74 | 146.811
0.149 | 3482.924 | 149.123 |  |  |  | 0.149 | 3567.35 | 145.261
0.15 | 3458.888 | 149.656 |  |  |  | 0.15 | 3372.556 | 145.699
0.151 | 3723.286 | 149.285 |  |  |  | 0.151 | 3758.203 | 145.394
0.152 | 3482.924 | 147.75 |  |  |  | 0.152 | 3506.6 | 143.668
0.153 | 3651.177 | 148.323 |  |  |  | 0.153 | 3631.416 | 144.35
0.154 | 3723.286 | 148.643 |  |  |  | 0.154 | 3836.784 | 144.801
0.155 | 3482.924 | 148.224 |  |  |  | 0.155 | 3506.6 | 144.443
0.156 | 3795.394 | 147.963 |  |  |  | 0.156 | 3770.747 | 143.697
0.157 | 3651.177 | 144.765 |  |  |  | 0.157 | 3631.416 | 140.787
0.158 | 3458.888 | 143.374 |  |  |  | 0.158 | 3524.431 | 139.669
0.159 | 3819.43 | 144.595 |  |  |  | 0.159 | 3720.571 | 140.316
0.16 | 3627.141 | 144.665 |  |  |  | 0.16 | 3613.585 | 140.583
0.161 | 3747.322 | 145.684 |  |  |  | 0.161 | 3613.585 | 142.297
0.162 | 3819.43 | 146.107 |  |  |  | 0.162 | 3809.726 | 142.646
0.163 | 3555.032 | 144.586 |  |  |  | 0.163 | 3595.754 | 140.494
0.164 | 3651.177 | 144.731 |  |  |  | 0.164 | 3649.247 | 140.766
0.165 | 3771.358 | 145.01 |  |  |  | 0.165 | 3756.233 | 141.26
0.166 | 3458.888 | 143.867 |  |  |  | 0.166 | 3488.769 | 140.23
0.167 | 3699.249 | 144.254 |  |  |  | 0.167 | 3631.416 | 140.861
0.168 | 3675.213 | 145.072 |  |  |  | 0.168 | 3702.74 | 140.881
0.169 | 3506.96 | 144.899 |  |  |  | 0.169 | 3577.923 | 140.131
0.17 | 3843.466 | 145.339 |  |  |  | 0.17 | 3738.402 | 140.468
0.171 | 3627.141 | 145.668 |  |  |  | 0.171 | 3702.74 | 141.136
0.172 | 3530.996 | 146.069 |  |  |  | 0.172 | 3595.754 | 141.87
0.173 | 3819.43 | 146.138 |  |  |  | 0.173 | 3774.064 | 142.089
0.174 | 3530.996 | 146.415 |  |  |  | 0.174 | 3542.262 | 142.193
0.175 | 3699.249 | 147.274 |  |  |  | 0.175 | 3560.092 | 142.891
0.176 | 3771.358 | 146.542 |  |  |  | 0.176 | 3720.571 | 142.298
0.177 | 3506.96 | 144.733 |  |  |  | 0.177 | 3542.262 | 141.331
0.178 | 3699.249 | 145.477 |  |  |  | 0.178 | 3684.909 | 141.893
0.179 | 3781.457 | 144.627 |  |  |  | 0.179 | 3756.233 | 140.847
0.18 | 3530.996 | 143.862 |  |  |  | 0.18 | 3542.262 | 139.781
0.181 | 3771.358 | 145.488 |  |  |  | 0.181 | 3702.74 | 141.361
0.182 | 3627.141 | 145.045 |  |  |  | 0.182 | 3667.078 | 140.974
0.183 | 3458.888 | 144.814 |  |  |  | 0.183 | 3524.431 | 140.986
0.184 | 3771.358 | 146.314 |  |  |  | 0.184 | 3702.74 | 142.156
0.185 | 3555.032 | 145.67 |  |  |  | 0.185 | 3613.585 | 141.512
0.186 | 3603.105 | 146.073 |  |  |  | 0.186 | 3613.585 | 142.238
0.187 | 3867.503 | 146.575 |  |  |  | 0.187 | 3791.895 | 142.713
0.188 | 3555.032 | 144.59 |  |  |  | 0.188 | 3613.585 | 140.884
0.189 | 3843.466 | 144.99 |  |  |  | 0.189 | 3649.247 | 141.236
0.19 | 3795.394 | 146.965 |  |  |  | 0.19 | 3720.571 | 142.845
0.191 | 3410.815 | 146.123 |  |  |  | 0.191 | 3506.6 | 142.449
0.192 | 3843.466 | 146.203 |  |  |  | 0.192 | 3613.585 | 142.572
0.193 | 3699.249 | 145.712 |  |  |  | 0.193 | 3667.078 | 141.896
0.194 | 3530.996 | 145.093 |  |  |  | 0.194 | 3542.262 | 141.225
0.195 | 3843.466 | 146.586 |  |  |  | 0.195 | 3756.233 | 143.13
0.196 | 3675.213 | 146.96 |  |  |  | 0.196 | 3667.078 | 143.924
0.197 | 3530.996 | 149.173 |  |  |  | 0.197 | 3560.092 | 145.079
0.198 | 3771.358 | 152.279 |  |  |  | 0.198 | 3738.402 | 147.023
0.199 | 3434.852 | 152.088 |  |  |  | 0.199 | 3524.431 | 147.196
0.2 | 3699.249 | 152.293 |  |  |  | 0.2 | 3524.431 | 147.773
0.201 | 3723.286 | 154.031 |  |  |  | 0.201 | 3649.247 | 148.931
0.202 | 3410.815 | 152.299 |  |  |  | 0.202 | 3488.769 | 148.252
0.203 | 3675.213 | 152.755 |  |  |  | 0.203 | 3613.585 | 148.6
0.204 | 3699.249 | 155.073 |  |  |  | 0.204 | 3649.247 | 150.278
0.205 | 3410.815 | 156.722 |  |  |  | 0.205 | 3435.276 | 152.185
0.206 | 3651.177 | 158.421 |  |  |  | 0.206 | 3595.754 | 153.829
0.207 | 3555.032 | 158.769 |  |  |  | 0.207 | 3524.431 | 154.487
0.208 | 3338.707 | 160.551 |  |  |  | 0.208 | 3346.121 | 155.898
0.209 | 3651.177 | 159.942 |  |  |  | 0.209 | 3577.923 | 155.586
0.21 | 3482.924 | 157.721 |  |  |  | 0.21 | 3470.938 | 154.273
0.211 | 3458.888 | 160.276 |  |  |  | 0.211 | 3453.107 | 156.119
0.212 | 3699.249 | 160.071 |  |  |  | 0.212 | 3649.247 | 155.547
0.213 | 3458.888 | 157.301 |  |  |  | 0.213 | 3470.938 | 153.868
0.214 | 3555.032 | 161.006 |  |  |  | 0.214 | 3488.769 | 156.911
0.215 | 3579.069 | 162.423 |  |  |  | 0.215 | 3542.262 | 158.3
0.216 | 3314.671 | 161.168 |  |  |  | 0.216 | 3328.29 | 157.458
0.217 | 3555.032 | 161.39 |  |  |  | 0.217 | 3453.107 | 156.99
0.218 | 3530.996 | 160.058 |  |  |  | 0.218 | 3506.6 | 155.301
0.219 | 3338.707 | 158.149 |  |  |  | 0.219 | 3417.445 | 154.117
0.22 | 3723.286 | 159.156 |  |  |  | 0.22 | 3577.923 | 155.306
0.221 | 3530.996 | 161.477 |  |  |  | 0.221 | 3506.6 | 157.189
0.222 | 3500.699 | 161.23 |  |  |  | 0.222 | 3417.445 | 156.811
0.223 | 3675.213 | 161.443 |  |  |  | 0.223 | 3613.585 | 157.156
0.224 | 3386.779 | 161.441 |  |  |  | 0.224 | 3399.614 | 157.156
0.225 | 3603.105 | 162.369 |  |  |  | 0.225 | 3417.445 | 158.126
0.226 | 3555.032 | 163.805 |  |  |  | 0.226 | 3542.262 | 159.738
0.227 | 3338.707 | 164.686 |  |  |  | 0.227 | 3363.952 | 160.735
0.228 | 3530.996 | 166.229 |  |  |  | 0.228 | 3435.276 | 162.283
0.229 | 3579.069 | 166.264 |  |  |  | 0.229 | 3506.6 | 162.029
0.23 | 3266.598 | 166.363 |  |  |  | 0.23 | 3310.459 | 162.586
0.231 | 3603.105 | 166.944 |  |  |  | 0.231 | 3470.938 | 162.916
0.232 | 3458.888 | 164.591 |  |  |  | 0.232 | 3417.445 | 160.451
0.233 | 3242.562 | 163.095 |  |  |  | 0.233 | 3310.459 | 159.187
0.234 | 3627.141 | 164.219 |  |  |  | 0.234 | 3506.6 | 160.359
0.235 | 3386.779 | 165.536 |  |  |  | 0.235 | 3399.614 | 161.335
0.236 | 3362.743 | 166.187 |  |  |  | 0.236 | 3399.614 | 161.855
0.237 | 3603.105 | 165.37 |  |  |  | 0.237 | 3595.754 | 161.228
0.238 | 3386.779 | 164.088 |  |  |  | 0.238 | 3399.614 | 159.685
0.239 | 3410.815 | 165.113 |  |  |  | 0.239 | 3453.107 | 160.657
0.24 | 3530.996 | 166.818 |  |  |  | 0.24 | 3524.431 | 162.272
0.241 | 3242.562 | 165.606 |  |  |  | 0.241 | 3274.797 | 161.415
0.242 | 3530.996 | 164.522 |  |  |  | 0.242 | 3417.445 | 160.883
0.243 | 3482.924 | 165.3 |  |  |  | 0.243 | 3488.769 | 161.414
0.244 | 3266.598 | 166.522 |  |  |  | 0.244 | 3328.29 | 162.71
0.245 | 3627.141 | 167.803 |  |  |  | 0.245 | 3524.431 | 163.717
0.246 | 3434.852 | 168.509 |  |  |  | 0.246 | 3435.276 | 164.242
0.247 | 3290.635 | 169.341 |  |  |  | 0.247 | 3363.952 | 164.339
0.248 | 3627.141 | 168.878 |  |  |  | 0.248 | 3524.431 | 163.684
0.249 | 3290.635 | 165.857 |  |  |  | 0.249 | 3328.29 | 162.346
0.25 | 3506.96 | 165.259 |  |  |  | 0.25 | 3363.952 | 161.801
0.251 | 3555.032 | 167.032 |  |  |  | 0.251 | 3524.431 | 163.164
0.252 | 3266.598 | 168.189 |  |  |  | 0.252 | 3292.628 | 163.725
0.253 | 3458.888 | 168.869 |  |  |  | 0.253 | 3417.445 | 165.007
0.254 | 3551.194 | 168.123 |  |  |  | 0.254 | 3506.6 | 165.135
0.255 | 3290.635 | 167.252 |  |  |  | 0.255 | 3328.29 | 163.349
0.256 | 3530.996 | 168.131 |  |  |  | 0.256 | 3470.938 | 163.494
0.257 | 3434.852 | 166.217 |  |  |  | 0.257 | 3453.107 | 161.769
0.258 | 3266.598 | 163.983 |  |  |  | 0.258 | 3328.29 | 160.606
0.259 | 3555.032 | 167.881 |  |  |  | 0.259 | 3506.6 | 163.738
0.26 | 3362.743 | 169.173 |  |  |  | 0.26 | 3399.614 | 165.058
0.261 | 3506.96 | 169.527 |  |  |  | 0.261 | 3381.783 | 165.88
0.262 | 3555.032 | 172.9 |  |  |  | 0.262 | 3524.431 | 168.01
0.263 | 3266.598 | 173.812 |  |  |  | 0.263 | 3328.29 | 169.279
0.264 | 3506.96 | 175.845 |  |  |  | 0.264 | 3346.121 | 171.46
0.265 | 3410.815 | 175.634 |  |  |  | 0.265 | 3417.445 | 170.897
0.266 | 3146.418 | 173.504 |  |  |  | 0.266 | 3203.473 | 168.611
0.267 | 3410.815 | 173.883 |  |  |  | 0.267 | 3328.29 | 169.178
0.268 | 3386.779 | 172.087 |  |  |  | 0.268 | 3399.614 | 168.244
0.269 | 3242.562 | 174.687 |  |  |  | 0.269 | 3274.797 | 171.315
0.27 | 3434.852 | 184.623 |  |  |  | 0.27 | 3399.614 | 176.212
0.271 | 3314.671 | 173.854 |  |  |  | 0.271 | 3346.121 | 171.35
0.272 | 3266.598 | 171.756 |  |  |  | 0.272 | 3328.29 | 168.69
0.273 | 3530.996 | 178.354 |  |  |  | 0.273 | 3470.938 | 174.273
0.274 | 3122.381 | 183.853 |  |  |  | 0.274 | 3203.473 | 179.24
0.275 | 3314.671 | 187.006 |  |  |  | 0.275 | 3149.981 | 182.688
0.276 | 3338.707 | 188.297 |  |  |  | 0.276 | 3292.628 | 184.498
0.277 | 3026.237 | 193.313 |  |  |  | 0.277 | 3096.488 | 189.791
0.278 | 3146.418 | 200.993 |  |  |  | 0.278 | 3132.15 | 197.223
0.279 | 3194.49 | 201.798 |  |  |  | 0.279 | 3149.981 | 197.871
0.28 | 2930.092 | 199.638 |  |  |  | 0.28 | 2953.84 | 195.748
0.281 | 3218.526 | 200.549 |  |  |  | 0.281 | 3149.981 | 196.623
0.282 | 3098.345 | 202.193 |  |  |  | 0.282 | 3060.826 | 198.463
0.283 | 2857.984 | 206.26 |  |  |  | 0.283 | 2882.516 | 202.443
0.284 | 3098.345 | 213.747 |  |  |  | 0.284 | 3060.826 | 208.966
0.285 | 2809.911 | 217.771 |  |  |  | 0.285 | 2882.516 | 214.818
0.286 | 2809.911 | 227.376 |  |  |  | 0.286 | 2775.53 | 221.08
0.287 | 3002.201 | 225.763 |  |  |  | 0.287 | 2936.009 | 221.935
0.288 | 2689.73 | 225.613 |  |  |  | 0.288 | 2757.7 | 224.372
0.289 | 2713.767 | 248.497 |  |  |  | 0.289 | 2668.545 | 238.883
0.29 | 2597.424 | 255.745 |  |  |  | 0.29 | 2579.39 | 250.016
0.291 | 2233.043 | 263.324 |  |  |  | 0.291 | 2347.588 | 261.289
0.292 | 2377.26 | 282.715 |  |  |  | 0.292 | 2329.757 | 275.368
0.293 | 2209.007 | 286.407 |  |  |  | 0.293 | 2187.109 | 282.672
0.294 | 2040.754 | 292.103 |  |  |  | 0.294 | 2044.461 | 293.341
0.295 | 1999.65 | 355.914 |  |  |  | 0.295 | 2008.8 | 363.228
0.296 | 965.859 | 446.456 |  |  |  | 0.296 | 1183.289 | 416.139
0.297 | 444.268 | 438.508 |  |  |  | 0.297 | 450.249 | 449.306
0.298 | 911.054 | 407.431 |  |  |  | 0.298 | 839.214 | 409.283
0.299 | 438.007 | 460.15 |  |  |  | 0.299 | 432.418 | 456.896

## Test-2188
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2188
Scenario | 480V - 20kA Available - A: calorimeter at 18", B: calorimeter at 6" Using simulated breaker , arc in open air
Test Voltage (V) | 434.9
Arc Current (A) | 10550
Arc Voltage (V) | 278.4
Duration of Arc (s) | 0.05134
Arc Energy (kJ) | 136.9 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.71 |  | Test 23-2188 was taken outside of the battery cabinet at the highest voltage and highest current. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A noticeable spark and smoke were observed. Review of high-speed video shows the arc grows towards the calorimeter placed in front of the battery cabinet, as well as away from the calorimeter towards the backside of the battery cabinet. It is then sustained evenly, before extinguishing. It was decided to proceed with the next test at the same current level.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 20000 | 0 | Incident Energy at 6" distance (cal/cm²) | 3.94
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 7017.442 | 44.395 |  |  |  | 0.109 | 1813.816 | 14.566
0.111 | 11113.973 | 147.484 |  |  |  | 0.11 | 6351.197 | 63.987
0.112 | 12806.044 | 201.967 |  |  |  | 0.111 | 11340.103 | 120.318
0.113 | 13795.475 | 214.135 |  |  |  | 0.112 | 12884.259 | 199.227
0.114 | 13967.55 | 217.449 |  |  |  | 0.113 | 13625.107 | 211.252
0.115 | 13408.306 | 219.965 |  |  |  | 0.114 | 13529.184 | 214.264
0.116 | 13666.419 | 222.237 |  |  |  | 0.115 | 13337.339 | 215.51
0.117 | 12935.1 | 222.052 |  |  |  | 0.116 | 13433.262 | 218.678
0.118 | 12806.044 | 221.596 |  |  |  | 0.117 | 12889.699 | 218.325
0.119 | 13064.156 | 223.588 |  |  |  | 0.118 | 12665.88 | 217.863
0.12 | 12633.969 | 225.758 |  |  |  | 0.119 | 12953.648 | 220.088
0.121 | 13107.175 | 228.545 |  |  |  | 0.12 | 12697.854 | 221.753
0.122 | 13193.212 | 230.19 |  |  |  | 0.121 | 13049.571 | 224.678
0.123 | 12633.969 | 229.768 |  |  |  | 0.122 | 12985.622 | 226.196
0.124 | 12978.119 | 230.856 |  |  |  | 0.123 | 12697.854 | 225.453
0.125 | 12849.062 | 231.115 |  |  |  | 0.124 | 12889.699 | 227.052
0.126 | 12074.725 | 232.384 |  |  |  | 0.125 | 12442.06 | 227.736
0.127 | 12547.931 | 236.172 |  |  |  | 0.126 | 12058.369 | 229.394
0.128 | 12203.781 | 237.606 |  |  |  | 0.127 | 12410.086 | 232.283
0.129 | 12289.819 | 240.473 |  |  |  | 0.128 | 12186.266 | 234.752
0.13 | 12633.969 | 244.482 |  |  |  | 0.129 | 12250.214 | 237.342
0.131 | 12117.744 | 245.171 |  |  |  | 0.13 | 12506.008 | 240.285
0.132 | 12203.781 | 246.095 |  |  |  | 0.131 | 12154.292 | 241.845
0.133 | 12074.725 | 241.699 |  |  |  | 0.132 | 12090.343 | 241.196
0.134 | 11515.481 | 236.163 |  |  |  | 0.133 | 11898.498 | 237.235
0.135 | 12074.725 | 236.915 |  |  |  | 0.134 | 11610.729 | 233.428
0.136 | 12074.725 | 237.121 |  |  |  | 0.135 | 11994.42 | 233.028
0.137 | 12031.706 | 239.747 |  |  |  | 0.136 | 11994.42 | 234.277
0.138 | 12504.912 | 244.645 |  |  |  | 0.137 | 12026.395 | 236.988
0.139 | 12504.912 | 244.294 |  |  |  | 0.138 | 12410.086 | 240.863
0.14 | 12031.706 | 240.904 |  |  |  | 0.139 | 12122.317 | 240.524
0.141 | 12375.856 | 238.573 |  |  |  | 0.14 | 12026.395 | 237.407
0.142 | 11816.612 | 234.711 |  |  |  | 0.141 | 12218.24 | 234.624
0.143 | 11945.669 | 234.876 |  |  |  | 0.142 | 11834.549 | 232.169
0.144 | 12289.819 | 239.955 |  |  |  | 0.143 | 11866.523 | 232.497
0.145 | 11859.631 | 246.333 |  |  |  | 0.144 | 12122.317 | 236.833
0.146 | 12160.762 | 253.747 |  |  |  | 0.145 | 11898.498 | 243.569
0.147 | 12074.725 | 256.895 |  |  |  | 0.146 | 12058.369 | 249.335
0.148 | 11515.481 | 258.541 |  |  |  | 0.147 | 11866.523 | 253.154
0.149 | 11644.537 | 262.127 |  |  |  | 0.148 | 11546.781 | 255.802
0.15 | 11386.425 | 264.427 |  |  |  | 0.149 | 11514.806 | 258.685
0.151 | 10647.486 | 276.628 |  |  |  | 0.15 | 11035.193 | 263.806
0.152 | 10483.031 | 294.895 |  |  |  | 0.151 | 10619.527 | 274.616
0.153 | 9782.195 | 317.574 |  |  |  | 0.152 | 10279.512 | 294.285
0.154 | 9192.469 | 334.793 |  |  |  | 0.153 | 9692.274 | 315.423
0.155 | 8592.911 | 340.046 |  |  |  | 0.154 | 9052.789 | 331.5
0.156 | 7815.869 | 350.12 |  |  |  | 0.155 | 8381.33 | 338.623
0.157 | 7136.542 | 383.921 |  |  |  | 0.156 | 7680.616 | 354.599
0.158 | 5664.931 | 410.408 |  |  |  | 0.157 | 6741.661 | 382.055
0.159 | 4847.575 | 427.531 |  |  |  | 0.158 | 5759.441 | 407.818
0.16 | 3998.631 | 445.012 |  |  |  | 0.159 | 4704.291 | 425.805
0.161 | 3040.787 | 452.064 |  |  |  | 0.16 | 3713.089 | 441.321
0.162 | 2868.712 | 468.715 |  |  |  | 0.161 | 3041.63 | 451.428
0.163 | 1857.771 | 490.814 |  |  |  | 0.162 | 2593.99 | 466.844
0.164 | 545.7 | 535.534 |  |  |  | 0.163 | 1874.704 | 498.022

## Test-2189
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2189
Scenario | 480V - 20kA Available - A: calorimeter at 18", B: calorimeter at 6" Using simulated breaker , arc in open air
Test Voltage (V) | 434.9
Arc Current (A) | 10550
Arc Voltage (V) | 273.1
Duration of Arc (s) | 0.06242
Arc Energy (kJ) | 168.8 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.99 |  | Test 23-2189 was taken outside of the battery cabinet at the highest voltage and highest current. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A noticeable spark and smoke were observed, leading to a small flame on the insulation block that contained the arc. As a result, the insulated cables were burned at the end that was fused. Review of high-speed video shows the arc grows towards the calorimeter placed in front of the battery cabinet, as well as away from the calorimeter towards the backside of the battery cabinet. It is then sustained evenly, before extinguishing. It was decided to proceed with tests inside the battery cabinet.
Electrode Gap (mm) | 21
Final Electrode Gap (mm) | 21 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 20000 | 0 | Incident Energy at 6" distance (cal/cm²) | 5.42
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 5643.838 | 79.643 |  |  |  | 0.109 | 1531.474 | 16.358
0.111 | 10053.15 | 157.842 |  |  |  | 0.11 | 5899.037 | 75.644
0.112 | 11988.888 | 193.909 |  |  |  | 0.111 | 10478.346 | 131.185
0.113 | 13064.275 | 219.25 |  |  |  | 0.112 | 12450.58 | 195.867
0.114 | 13150.307 | 223.574 |  |  |  | 0.113 | 13428.626 | 214.978
0.115 | 12720.146 | 224.814 |  |  |  | 0.115 | 12883.532 | 223.411
0.116 | 13064.275 | 225.313 |  |  |  | 0.116 | 13204.149 | 223.562
0.117 | 12526.573 | 221.324 |  |  |  | 0.117 | 12643.021 | 219.987
0.118 | 12419.033 | 217.504 |  |  |  | 0.118 | 12594.89 | 216.39
0.119 | 12892.21 | 218.777 |  |  |  | 0.119 | 12947.64 | 217.161
0.12 | 12634.113 | 220.749 |  |  |  | 0.12 | 12755.231 | 219.247
0.121 | 12978.242 | 224.638 |  |  |  | 0.121 | 13011.776 | 223.195
0.122 | 13193.323 | 230.109 |  |  |  | 0.122 | 13140.049 | 228.776
0.123 | 12677.097 | 235.321 |  |  |  | 0.123 | 12626.958 | 233.254
0.124 | 12548.081 | 236.014 |  |  |  | 0.124 | 12659.027 | 234.081
0.125 | 12246.984 | 234.309 |  |  |  | 0.125 | 12306.277 | 232.165
0.126 | 11687.759 | 231.143 |  |  |  | 0.126 | 11889.392 | 229.518
0.127 | 12160.936 | 228.822 |  |  |  | 0.127 | 12210.073 | 227.244
0.128 | 12160.936 | 229.112 |  |  |  | 0.128 | 12274.209 | 227.856
0.129 | 12246.968 | 234.28 |  |  |  | 0.129 | 12370.413 | 233.023
0.13 | 12634.113 | 239.711 |  |  |  | 0.13 | 12659.027 | 237.517
0.131 | 12160.936 | 242.205 |  |  |  | 0.131 | 12306.277 | 240.124
0.132 | 12203.925 | 242.892 |  |  |  | 0.132 | 12145.937 | 241.036
0.133 | 11988.882 | 240.997 |  |  |  | 0.133 | 11985.596 | 238.674
0.134 | 11429.662 | 240.397 |  |  |  | 0.134 | 11632.846 | 238.355
0.135 | 11730.775 | 242.96 |  |  |  | 0.135 | 11793.187 | 241.574
0.136 | 11730.775 | 246.244 |  |  |  | 0.136 | 11761.119 | 244.345
0.137 | 11386.646 | 247.554 |  |  |  | 0.137 | 11600.778 | 245.8
0.138 | 11945.856 | 249.824 |  |  |  | 0.138 | 11985.596 | 247.749
0.139 | 11773.791 | 249.421 |  |  |  | 0.139 | 11793.187 | 247.918
0.14 | 11558.71 | 251.21 |  |  |  | 0.14 | 11632.846 | 249.414
0.141 | 11687.759 | 254.673 |  |  |  | 0.141 | 11664.915 | 252.875
0.142 | 11214.582 | 255.23 |  |  |  | 0.142 | 11119.756 | 253.94
0.143 | 10870.453 | 255.053 |  |  |  | 0.143 | 11023.552 | 253.625
0.144 | 11171.565 | 254.873 |  |  |  | 0.144 | 11215.961 | 253.428
0.145 | 10827.436 | 253.475 |  |  |  | 0.145 | 11055.62 | 252.479
0.146 | 11300.614 | 253.026 |  |  |  | 0.146 | 11408.37 | 251.996
0.147 | 11558.71 | 252.87 |  |  |  | 0.147 | 11504.574 | 251.881
0.148 | 11128.549 | 253.687 |  |  |  | 0.148 | 11312.165 | 252.854
0.149 | 11472.678 | 255.235 |  |  |  | 0.149 | 11536.642 | 253.624
0.15 | 11386.646 | 253.61 |  |  |  | 0.15 | 11151.825 | 251.805
0.151 | 10698.388 | 252.263 |  |  |  | 0.151 | 10895.28 | 251.331
0.152 | 11171.565 | 256.098 |  |  |  | 0.152 | 11280.097 | 255.717
0.153 | 10913.469 | 265.097 |  |  |  | 0.153 | 11023.552 | 264.174
0.154 | 10827.436 | 275.234 |  |  |  | 0.154 | 10927.348 | 273.072
0.155 | 10827.436 | 279.658 |  |  |  | 0.155 | 10863.211 | 277.945
0.156 | 10268.227 | 279.791 |  |  |  | 0.156 | 10478.394 | 279.288
0.157 | 10311.243 | 285.882 |  |  |  | 0.157 | 10382.189 | 276.295
0.158 | 10053.146 | 263.472 |  |  |  | 0.159 | 10189.781 | 243.073
0.159 | 10182.195 | 241.837 |  |  |  | 0.16 | 10734.895 | 276.515
0.16 | 10698.388 | 271.457 |  |  |  | 0.161 | 10221.861 | 312.303
0.161 | 9988.622 | 318.338 |  |  |  | 0.162 | 9227.737 | 333.943
0.162 | 9063.776 | 336.32 |  |  |  | 0.163 | 8682.579 | 344.413
0.163 | 8676.631 | 344.954 |  |  |  | 0.164 | 7752.603 | 358.357
0.164 | 7601.228 | 359.684 |  |  |  | 0.165 | 6982.968 | 372.488
0.165 | 7042.018 | 374.444 |  |  |  | 0.166 | 6181.265 | 377.035
0.166 | 6396.776 | 378.653 |  |  |  | 0.167 | 5636.106 | 376.581
0.167 | 5665.47 | 378.075 |  |  |  | 0.168 | 5475.782 | 379.388
0.168 | 5579.47 | 382.496 |  |  |  | 0.169 | 4962.7 | 388.027
0.169 | 4977.244 | 387.77 |  |  |  | 0.171 | 4032.755 | 461.108
0.17 | 4977.244 | 418.963 |  |  |  | 0.172 | 1820.018 | 526.318
0.171 | 4073.906 | 465.018
0.172 | 2288.737 | 516.631
0.173 | 847.681 | 543.73

## Test-2190
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2190
Scenario | 190V - 5kA Available Arc on battery side of breaker with Cabinet
Test Voltage (V) | 173.8
Arc Current (A) | 2392
Arc Voltage (V) | 117.9
Duration of Arc (s) | 0.01776
Arc Energy (kJ) | 4.666 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.02 |  | Test 23-2190 was taken inside of the battery cabinet at the lowest voltage and lowest current. The voltage was achieved as per Test 23-2176, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at the same voltage level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 192
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 0.03
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.111 | 4134.321 | 14.365 |  |  |  | 0.111 | 4076.586 | 14.73
0.112 | 5009.552 | 20.172 |  |  |  | 0.112 | 4995.561 | 29.735
0.113 | 4305.735 | 68.991 |  |  |  | 0.113 | 4217.981 | 67.756
0.114 | 3216.395 | 115.822 |  |  |  | 0.114 | 3393.474 | 104.381
0.115 | 2661.37 | 112.886 |  |  |  | 0.115 | 2759.238 | 119.518
0.116 | 2405.205 | 114.543 |  |  |  | 0.116 | 2410.408 | 108.302
0.117 | 2447.899 | 116.292 |  |  |  | 0.117 | 2480.43 | 120.611
0.118 | 2405.205 | 118.639 |  |  |  | 0.118 | 2378.696 | 112.844
0.119 | 2149.04 | 120.494 |  |  |  | 0.119 | 2156.713 | 120.441
0.12 | 2362.511 | 122.468 |  |  |  | 0.12 | 2388.593 | 117.642
0.121 | 2191.734 | 123.924 |  |  |  | 0.121 | 2188.425 | 124.014
0.122 | 2020.957 | 127.46 |  |  |  | 0.122 | 2033.165 | 125.935
0.123 | 2191.734 | 123.073 |  |  |  | 0.123 | 2195.023 | 127.298
0.124 | 2149.04 | 112.082 |  |  |  | 0.124 | 2125.001 | 112.138
0.125 | 2266.976 | 122.809 |  |  |  | 0.125 | 2125.001 | 127.486
0.126 | 2119.874 | 125.777 |  |  |  | 0.126 | 2258.447 | 122.799
0.128 | 2050.123 | 136.84 |  |  |  | 0.127 | 1998.154 | 130.012
0.129 | 1827.779 | 166.855 |  |  |  | 0.128 | 2068.176 | 137.605
0.13 | 796.99 | 208.34 |  |  |  | 0.129 | 1599.097 | 170.997
[6 empty] | 0.13 | 838.074 | 206.429

## Test-2191
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2191
Scenario | 190V - 5kA Available Arc on battery side of breaker with Cabinet A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 173.8
Arc Current (A) | 2191
Arc Voltage (V) | 130.6
Duration of Arc (s) | 0.01093
Arc Energy (kJ) | 2.62 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.02 |  | Test 23-2191 was taken inside of the battery cabinet at the lowest voltage and lowest current. The voltage was achieved as per Test 23-2176, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at a higher voltage level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 190
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 0.02
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.1105 | 2877.848 | 16.3648 |  |  |  | 0.1105 | 2845.508 | 18.5942
0.111 | 3948.709 | 25.302 |  |  |  | 0.111 | 3892.762 | 24.9726
0.1115 | 4419.888 | 30.4992 |  |  |  | 0.1115 | 4400.521 | 30.1058
0.112 | 4676.895 | 34.8402 |  |  |  | 0.112 | 4654.401 | 33.44
0.1125 | 4634.061 | 38.8726 |  |  |  | 0.1125 | 4590.931 | 38.2254
0.113 | 4505.557 | 51.9808 |  |  |  | 0.113 | 4463.991 | 54.0549
0.1135 | 4034.378 | 85.637 |  |  |  | 0.1135 | 3924.497 | 86.1625
0.114 | 3434.696 | 111.7008 |  |  |  | 0.114 | 3448.472 | 115.4687
0.1145 | 3134.855 | 112.7433 |  |  |  | 0.1145 | 3131.123 | 112.2058
0.115 | 2963.517 | 115.7003 |  |  |  | 0.115 | 2908.978 | 115.4938
0.1155 | 2492.338 | 126.8625 |  |  |  | 0.1155 | 2464.688 | 127.1727
0.116 | 2106.828 | 130.0717 |  |  |  | 0.116 | 2147.339 | 130.9673
0.1165 | 2063.993 | 128.8278 |  |  |  | 0.1165 | 2052.134 | 127.2953
0.117 | 2192.496 | 129.1045 |  |  |  | 0.117 | 2179.074 | 128.9297
0.1175 | 2149.662 | 135.7865 |  |  |  | 0.1175 | 2115.604 | 135.7625
0.118 | 1935.49 | 137.6079 |  |  |  | 0.118 | 1893.459 | 135.8175
0.1185 | 1764.152 | 136.815 |  |  |  | 0.1185 | 1734.784 | 136.046
0.119 | 1721.317 | 143.5782 |  |  |  | 0.119 | 1671.314 | 142.5051
0.1195 | 1721.317 | 150.6143 |  |  |  | 0.1195 | 1671.314 | 152.0969
0.12 | 1721.317 | 151.5664 |  |  |  | 0.12 | 1671.314 | 150.9425
0.1205 | 1592.814 | 153.1855 |  |  |  | 0.1205 | 1576.109 | 153.3008
0.121 | 1335.807 | 163.0695 |  |  |  | 0.121 | 1290.494 | 162.7606
0.1215 | 1035.966 | 175.8302 |  |  |  | 0.1215 | 1004.88 | 175.3404
0.122 | 821.794 | 190.0859 |  |  |  | 0.122 | 814.47 | 189.521
0.1225 | 650.456 | 205.2742 |  |  |  | 0.1225 | 576.642 | 204.1254
0.123 | 307.78 | 209.6073

## Test-2192
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2192
Scenario | 240V - 5kA Available Arc on battery side of breaker with Cabinet A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 271.7
Arc Current (A) | 2586
Arc Voltage (V) | 155.2
Duration of Arc (s) | 0.05702
Arc Energy (kJ) | 22.78 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.12 |  | Test 23-2192 was taken inside of the battery cabinet at intermediate voltage and lowest current. The voltage was achieved as per Test 23-2177, and the current was approximately achieved. A noticeable spark and smoke were observed, leading to a small flame near the terminals of the circuit breaker. Review of high-speed video shows the arc grow towards the calorimeter placed in front of the batter cabinet, before extinguishing. It was decided to proceed with the next test at the same voltage level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 240
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 0.28
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.1105 | 4037.544 | 34.0282 |  |  |  | 0.11 | 2785.392 | 24.0029
0.111 | 4722.698 | 45.9951 |  |  |  | 0.1105 | 4092.294 | 31.4085
0.1115 | 5418.811 | 60.8901 |  |  |  | 0.111 | 4812.149 | 42.3536
0.112 | 5236.563 | 90.3224 |  |  |  | 0.1115 | 5325.735 | 57.3592
0.1125 | 4380.121 | 122.8906 |  |  |  | 0.112 | 5325.735 | 89.7752
0.113 | 3866.256 | 131.6521 |  |  |  | 0.1125 | 4728.758 | 124.6255
0.1135 | 3438.035 | 138.6362 |  |  |  | 0.113 | 3861.865 | 130.9411
0.114 | 3266.746 | 140.7278 |  |  |  | 0.1135 | 3543.633 | 137.0928
0.1145 | 3266.746 | 142.8765 |  |  |  | 0.114 | 3416.34 | 140.4407
0.115 | 3266.746 | 142.867 |  |  |  | 0.1145 | 3352.694 | 142.6252
0.1155 | 3009.814 | 145.0817 |  |  |  | 0.115 | 3225.401 | 142.7353
0.116 | 2752.881 | 152.6949 |  |  |  | 0.1155 | 3161.754 | 143.4635
0.1165 | 2581.593 | 162.6781 |  |  |  | 0.116 | 2843.522 | 149.871
0.117 | 2581.593 | 169.0115 |  |  |  | 0.1165 | 2716.229 | 159.835
0.1175 | 2581.593 | 172.8511 |  |  |  | 0.117 | 2652.582 | 167.493
0.118 | 2239.016 | 173.3951 |  |  |  | 0.1175 | 2588.936 | 171.9414
0.1185 | 1896.439 | 171.5752 |  |  |  | 0.118 | 2397.996 | 173.4237
0.119 | 1982.084 | 168.636 |  |  |  | 0.1185 | 2079.764 | 171.3765
0.1195 | 2324.66 | 169.7149 |  |  |  | 0.119 | 2143.41 | 168.9637
0.12 | 2324.66 | 166.3825 |  |  |  | 0.1195 | 2397.996 | 161.0179
0.1205 | 2410.304 | 161.4998 |  |  |  | 0.12 | 2461.643 | 174.6901
0.121 | 2581.593 | 150.9285 |  |  |  | 0.1205 | 2461.643 | 160.2422
0.1215 | 2410.304 | 145.6415 |  |  |  | 0.121 | 2588.936 | 148.8006
0.122 | 2581.593 | 148.2173 |  |  |  | 0.1215 | 2588.936 | 145.449
0.1225 | 2752.881 | 150.4723 |  |  |  | 0.122 | 2652.582 | 146.7567
0.123 | 2924.17 | 152.9319 |  |  |  | 0.1225 | 2907.168 | 149.9171
0.1235 | 2752.881 | 152.1363 |  |  |  | 0.123 | 2970.815 | 152.6543
0.124 | 2495.949 | 148.2227 |  |  |  | 0.1235 | 2843.522 | 152.6928
0.1245 | 2495.949 | 143.8167 |  |  |  | 0.124 | 2588.936 | 149.0849
0.125 | 2838.525 | 142.3268 |  |  |  | 0.1245 | 2652.582 | 142.4985
0.1255 | 3095.458 | 145.3416 |  |  |  | 0.125 | 2907.168 | 139.6005
0.126 | 2924.17 | 151.884 |  |  |  | 0.1255 | 3161.754 | 142.294
0.1265 | 2752.881 | 155.6655 |  |  |  | 0.126 | 3098.108 | 148.6511
0.127 | 2410.304 | 156.3525 |  |  |  | 0.1265 | 2779.875 | 153.5889
0.1275 | 2495.949 | 156.9041 |  |  |  | 0.127 | 2588.936 | 155.0949
0.128 | 2752.881 | 155.8267 |  |  |  | 0.1275 | 2588.936 | 155.012
0.1285 | 2752.881 | 154.6847 |  |  |  | 0.128 | 2843.522 | 154.3695
0.129 | 2752.881 | 154.2771 |  |  |  | 0.1285 | 2907.168 | 153.1313
0.1295 | 2581.593 | 157.9112 |  |  |  | 0.129 | 2907.168 | 152.4298
0.13 | 2239.016 | 162.9411 |  |  |  | 0.1295 | 2716.229 | 156.0498
0.1305 | 2239.016 | 165.0827 |  |  |  | 0.13 | 2397.996 | 160.5931
0.131 | 2581.593 | 162.4117 |  |  |  | 0.1305 | 2461.643 | 163.1355
0.1315 | 2581.593 | 157.7432 |  |  |  | 0.131 | 2588.936 | 162.0157
0.132 | 2495.949 | 155.494 |  |  |  | 0.1315 | 2716.229 | 156.7391
0.1325 | 2410.304 | 155.7517 |  |  |  | 0.132 | 2588.936 | 154.1271
0.133 | 2410.304 | 156.7598 |  |  |  | 0.1325 | 2461.643 | 153.5841
0.1335 | 2581.593 | 156.673 |  |  |  | 0.133 | 2461.643 | 155.0945
0.134 | 2752.881 | 155.1658 |  |  |  | 0.1335 | 2652.582 | 155.8306
0.1345 | 2752.881 | 154.3455 |  |  |  | 0.134 | 2843.522 | 154.212
0.135 | 2495.949 | 155.1187 |  |  |  | 0.1345 | 2716.229 | 152.9883
0.1355 | 2410.304 | 155.3761 |  |  |  | 0.135 | 2588.936 | 153.1856
0.136 | 2495.949 | 154.8754 |  |  |  | 0.1355 | 2461.643 | 154.032
0.1365 | 2752.881 | 159.4 |  |  |  | 0.136 | 2652.582 | 153.1416
0.137 | 2752.881 | 162.5296 |  |  |  | 0.1365 | 2843.522 | 156.7985
0.1375 | 2410.304 | 162.9453 |  |  |  | 0.137 | 2843.522 | 168.2421
0.138 | 2410.304 | 159.8005 |  |  |  | 0.1375 | 2588.936 | 161.4015
0.1385 | 2410.304 | 156.8398 |  |  |  | 0.138 | 2461.643 | 158.99
0.139 | 2581.593 | 156.8628 |  |  |  | 0.1385 | 2461.643 | 155.713
0.1395 | 2752.881 | 156.738 |  |  |  | 0.139 | 2588.936 | 155.7182
0.14 | 2752.881 | 157.1725 |  |  |  | 0.1395 | 2843.522 | 155.1002
0.1405 | 2495.949 | 154.9825 |  |  |  | 0.14 | 2843.522 | 155.3461
0.141 | 2324.66 | 155.1375 |  |  |  | 0.1405 | 2525.289 | 154.1696
0.1415 | 2581.593 | 154.7569 |  |  |  | 0.141 | 2461.643 | 154.7766
0.142 | 2581.593 | 157.0163 |  |  |  | 0.1415 | 2588.936 | 155.0581
0.1425 | 2667.237 | 161.6021 |  |  |  | 0.142 | 2716.229 | 156.6051
0.143 | 2495.949 | 163.8795 |  |  |  | 0.1425 | 2716.229 | 160.7507
0.1435 | 2239.016 | 166.2721 |  |  |  | 0.143 | 2588.936 | 163.5767
0.144 | 2067.728 | 168.062 |  |  |  | 0.1435 | 2334.35 | 165.2545
0.1445 | 2324.66 | 170.8039 |  |  |  | 0.144 | 2207.057 | 167.0959
0.145 | 2410.304 | 169.1812 |  |  |  | 0.1445 | 2334.35 | 169.2663
0.1455 | 2410.304 | 165.6036 |  |  |  | 0.145 | 2461.643 | 168.7734
0.146 | 2410.304 | 156.4775 |  |  |  | 0.1455 | 2461.643 | 165.5571
0.1465 | 2410.304 | 152.0228 |  |  |  | 0.146 | 2461.643 | 156.9263
0.147 | 2581.593 | 150.0518 |  |  |  | 0.1465 | 2461.643 | 150.6098
0.1475 | 2752.881 | 153.7952 |  |  |  | 0.147 | 2588.936 | 148.3874
0.148 | 2838.525 | 159.313 |  |  |  | 0.1475 | 2843.522 | 150.6708
0.1485 | 2581.593 | 163.791 |  |  |  | 0.148 | 2843.522 | 156.7745
0.149 | 2239.016 | 168.5851 |  |  |  | 0.1485 | 2716.229 | 161.3802
0.1495 | 2067.728 | 169.0526 |  |  |  | 0.149 | 2397.996 | 166.6438
0.15 | 2239.016 | 165.5777 |  |  |  | 0.1495 | 2207.057 | 168.0974
0.1505 | 2410.304 | 161.3792 |  |  |  | 0.15 | 2334.35 | 165.4148
0.151 | 2581.593 | 157.6565 |  |  |  | 0.1505 | 2525.289 | 161.0476
0.1515 | 2410.304 | 159.306 |  |  |  | 0.151 | 2716.229 | 156.6926
0.152 | 2239.016 | 164.5888 |  |  |  | 0.1515 | 2525.289 | 157.5197
0.1525 | 2239.016 | 164.7935 |  |  |  | 0.152 | 2334.35 | 162.66
0.153 | 2410.304 | 162.0491 |  |  |  | 0.1525 | 2207.057 | 163.4775
0.1535 | 2581.593 | 156.1328 |  |  |  | 0.153 | 2525.289 | 160.8176
0.154 | 2752.881 | 154.3936 |  |  |  | 0.1535 | 2716.229 | 155.0939
0.1545 | 2581.593 | 157.4545 |  |  |  | 0.154 | 2779.875 | 152.9376
0.155 | 2324.66 | 161.9524 |  |  |  | 0.1545 | 2588.936 | 155.5327
0.1555 | 2410.304 | 165.4209 |  |  |  | 0.155 | 2461.643 | 160.3309
0.156 | 2581.593 | 165.8826 |  |  |  | 0.1555 | 2461.643 | 163.6996
0.1565 | 2581.593 | 168.4544 |  |  |  | 0.156 | 2588.936 | 164.7404
0.157 | 2239.016 | 173.043 |  |  |  | 0.1565 | 2588.936 | 166.8011
0.1575 | 1982.084 | 177.096 |  |  |  | 0.157 | 2397.996 | 170.9586
0.158 | 1896.439 | 174.2041 |  |  |  | 0.1575 | 2016.117 | 174.5063
0.1585 | 2239.016 | 169.1712 |  |  |  | 0.158 | 1952.471 | 172.6805
0.159 | 2410.304 | 163.2065 |  |  |  | 0.1585 | 2270.703 | 167.7235
0.1595 | 2410.304 | 159.8852 |  |  |  | 0.159 | 2461.643 | 162.6294
0.16 | 2324.66 | 160.0005 |  |  |  | 0.1595 | 2461.643 | 158.347
0.1605 | 2239.016 | 162.8785 |  |  |  | 0.16 | 2461.643 | 158.9687
0.161 | 2239.016 | 167.1889 |  |  |  | 0.1605 | 2334.35 | 161.7738
0.1615 | 2410.304 | 171.2702 |  |  |  | 0.161 | 2334.35 | 165.9448
0.162 | 2495.949 | 175.4895 |  |  |  | 0.1615 | 2588.936 | 169.6314
0.1625 | 2067.728 | 175.5635 |  |  |  | 0.162 | 2588.936 | 173.8484
0.163 | 1896.439 | 170.6926 |  |  |  | 0.1625 | 2270.703 | 179.6184
0.1635 | 2067.728 | 161.9984 |  |  |  | 0.163 | 1952.471 | 170.5806
0.164 | 2495.949 | 157.316 |  |  |  | 0.1635 | 2270.703 | 160.4357
0.1645 | 2581.593 | 159.9251 |  |  |  | 0.164 | 2525.289 | 157.1599
0.165 | 2581.593 | 164.7412 |  |  |  | 0.1645 | 2716.229 | 158.6903
0.1655 | 2239.016 | 161.8419 |  |  |  | 0.165 | 2652.582 | 163.399
0.166 | 2153.372 | 161.0782 |  |  |  | 0.1655 | 2270.703 | 161.5002
0.1665 | 2410.304 | 159.5303 |  |  |  | 0.166 | 2207.057 | 160.0734
0.167 | 2581.593 | 162.3743 |  |  |  | 0.1665 | 2461.643 | 159.0728
0.1675 | 2581.593 | 163.8428 |  |  |  | 0.167 | 2588.936 | 161.1405
0.168 | 2410.304 | 162.4888 |  |  |  | 0.1675 | 2588.936 | 163.0835
0.1685 | 2239.016 | 165.1327 |  |  |  | 0.168 | 2588.936 | 161.4775
0.169 | 2153.372 | 180.82 |  |  |  | 0.1685 | 2334.35 | 159.9539
0.1695 | 1639.507 | 240.6636 |  |  |  | 0.169 | 2143.41 | 185.8331
[6 empty] | 0.1695 | 1716.526 | 243.1803
[6 empty] | 0.17 | 951.665 | 289.3752

## Test-2193
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2193
Scenario | 240V - 5kA Available Arc on battery side of breaker with Cabinet A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 271.7
Arc Current (A) | 3181
Arc Voltage (V) | 148
Duration of Arc (s) | 0.01149
Arc Energy (kJ) | 4.832 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.02 |  | Test 23-2193 was taken inside of the battery cabinet at intermediate voltage and lowest current. The voltage was achieved as per Test 23-2177, and the current was approximately achieved. A noticeable spark and smoke were observed. It was decided to proceed with the next test at a higher voltage level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 240
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 0.04
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.111 | 4581.171 | 17.8589 |  |  |  | 0.1109 | 4614.805 | 20.3456
0.1115 | 5700.549 | 26.3675 |  |  |  | 0.1112 | 5226.702 | 25.1122
0.112 | 6131.079 | 41.9968 |  |  |  | 0.1115 | 5662.304 | 27.5612
0.1125 | 5614.443 | 80.8932 |  |  |  | 0.112 | 5982.089 | 57.2337
0.113 | 4925.595 | 117.4881 |  |  |  | 0.1125 | 5664.596 | 94.759
0.1135 | 4150.64 | 123.6941 |  |  |  | 0.1129 | 5094.756 | 112.3073
0.114 | 3978.429 | 124.3074 |  |  |  | 0.1132 | 4521.436 | 121.1388
0.1145 | 3978.429 | 125.8261 |  |  |  | 0.1135 | 4063.384 | 122.1743
0.115 | 3892.322 | 127.9842 |  |  |  | 0.114 | 3935.47 | 126.475
0.1155 | 3634.004 | 128.2842 |  |  |  | 0.1145 | 3935.47 | 128.2589
0.116 | 3375.686 | 127.4517 |  |  |  | 0.115 | 3807.557 | 128.9497
0.1165 | 3375.686 | 125.0887 |  |  |  | 0.1155 | 3487.772 | 128.744
0.117 | 3634.004 | 123.9857 |  |  |  | 0.116 | 3231.945 | 128.6711
0.1175 | 3720.11 | 124.0638 |  |  |  | 0.1165 | 3359.859 | 128.0308
0.118 | 3547.898 | 124.305 |  |  |  | 0.117 | 3551.729 | 127.8798
0.1185 | 3375.686 | 126.463 |  |  |  | 0.1175 | 3679.643 | 128.1544
0.119 | 3289.58 | 131.5687 |  |  |  | 0.118 | 3487.772 | 125.9842
0.1195 | 3375.686 | 141.039 |  |  |  | 0.1185 | 3359.859 | 125.5828
0.12 | 3375.686 | 151.044 |  |  |  | 0.119 | 3231.945 | 136.4652
0.1205 | 3203.474 | 159.9396 |  |  |  | 0.1195 | 3295.902 | 145.456
0.121 | 2859.05 | 168.6122 |  |  |  | 0.12 | 3295.902 | 153.7601
0.1215 | 2428.52 | 191.2395 |  |  |  | 0.1205 | 3104.032 | 163.7578
0.122 | 1825.778 | 220.5751 |  |  |  | 0.121 | 2720.291 | 163.4276
0.1225 | 1481.354 | 236.7108 |  |  |  | 0.1215 | 2208.636 | 197.9737
0.123 | 967.054 | 272.1714 |  |  |  | 0.122 | 1760.938 | 221.1625
[6 empty] | 0.1225 | 1441.154 | 237.5312
[6 empty] | 0.123 | 801.586 | 266.8301

## Test-2194
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2194
Scenario | 480V - 5kA Available Arc on battery side of breaker with Cabinet A: calorimeter at 18", 66" high, angled to breaker terminals: B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 434.9
Arc Current (A) | 2160
Arc Voltage (V) | 274.3
Duration of Arc (s) | 0.9987
Arc Energy (kJ) | 572.3 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 4.68 |  | Test 23-2194 was taken inside of the battery cabinet at highest voltage and lowest current. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A significant blast and black smoke were observed, followed by a fire near the terminals of the circuit breaker. As a result, this side of the circuit breaker could no longer be used. Review of the high-speed video shows a substantial “ball of flame” grow towards the calorimeter placed in front of the batter cabinet, and extend beyond frame. It is then sustained in this manner for a significant period of time. Smoke and flames can be seen to begin exhausting near the top of the battery cabinet as the arc began to extinguish. Nonetheless, it was decided to proceed with the next test at a same voltage level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 7.76
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.112 | 4664.444 | 47.025 |  |  |  | 0.11 | 3004.686 | 37.586
0.115 | 3807.161 | 111.625 |  |  |  | 0.115 | 4769.851 | 98.618
0.12 | 3550.836 | 147.207 |  |  |  | 0.12 | 3550.836 | 142.947
0.125 | 3379.953 | 155.962 |  |  |  | 0.125 | 3379.953 | 155.81
0.13 | 3422.674 | 181.147 |  |  |  | 0.13 | 3057.207 | 216.561
0.132 | 2701.544 | 238.715 |  |  |  | 0.132 | 2701.544 | 244.328
0.135 | 1756.564 | 335.812 |  |  |  | 0.135 | 1756.564 | 298.01
0.14 | 1884.726 | 295.836 |  |  |  | 0.14 | 1884.726 | 313.689
0.145 | 1671.122 | 328.737 |  |  |  | 0.145 | 1671.122 | 335.196
0.15 | 1970.168 | 292.567 |  |  |  | 0.15 | 1970.168 | 317.411
0.155 | 1842.006 | 316.846 |  |  |  | 0.155 | 1842.006 | 305.041
0.16 | 1970.168 | 308.632 |  |  |  | 0.16 | 1970.168 | 308.488
0.165 | 1927.447 | 300.67 |  |  |  | 0.165 | 1927.447 | 306.869
0.17 | 1927.447 | 335.37 |  |  |  | 0.17 | 1927.447 | 298.896
0.175 | 1799.285 | 314.935 |  |  |  | 0.175 | 1799.285 | 311.423
0.18 | 1927.447 | 309.152 |  |  |  | 0.18 | 1927.447 | 310.979
0.185 | 1671.122 | 337.752 |  |  |  | 0.185 | 1671.122 | 318.64
0.19 | 2098.33 | 275.735 |  |  |  | 0.19 | 2098.33 | 302.707
0.195 | 1756.564 | 321.142 |  |  |  | 0.195 | 1756.564 | 315.456
0.2 | 1414.798 | 358.823 |  |  |  | 0.2 | 1414.798 | 317.07
0.205 | 1671.122 | 331.102 |  |  |  | 0.205 | 1671.122 | 296.29
0.209 | 2192.377 | 275.252 |  |  |  | 0.209 | 2192.377 | 298.148
0.215 | 1671.122 | 355.429 |  |  |  | 0.215 | 1671.122 | 326.811
0.22 | 2183.772 | 282.786 |  |  |  | 0.22 | 2183.772 | 303.43
0.225 | 1927.447 | 326.476 |  |  |  | 0.225 | 1927.447 | 307.274
0.23 | 2098.33 | 291.425 |  |  |  | 0.23 | 2098.33 | 301.404
0.235 | 2226.492 | 274.58 |  |  |  | 0.235 | 2226.492 | 284.021
0.24 | 1913.104 | 325.307 |  |  |  | 0.24 | 1913.104 | 316.329
0.245 | 1970.168 | 296.568 |  |  |  | 0.245 | 1970.168 | 311.068
0.25 | 2183.772 | 301.047 |  |  |  | 0.25 | 2183.772 | 304.421
0.255 | 1799.285 | 349.64 |  |  |  | 0.255 | 1799.285 | 325.82
0.26 | 1756.564 | 316.59 |  |  |  | 0.26 | 1756.564 | 307.679
0.265 | 2055.609 | 291.134 |  |  |  | 0.265 | 2055.609 | 306.165
0.27 | 1799.285 | 329.649 |  |  |  | 0.27 | 1799.285 | 318.69
0.275 | 2012.889 | 297.273 |  |  |  | 0.275 | 2012.889 | 304.086
0.28 | 1893.332 | 276.684 |  |  |  | 0.28 | 1893.332 | 284.166
0.282 | 2519.801 | 251.646 |  |  |  | 0.282 | 2519.801 | 283.931
0.285 | 2010.02 | 290.866 |  |  |  | 0.285 | 2010.02 | 297.633
0.29 | 1671.122 | 314.143 |  |  |  | 0.29 | 1671.122 | 315.501
0.295 | 2055.609 | 264.543 |  |  |  | 0.295 | 2055.609 | 287.423
0.3 | 2183.772 | 289.487 |  |  |  | 0.3 | 2183.772 | 294.239
0.305 | 1634.139 | 349.899 |  |  |  | 0.305 | 1634.139 | 340.443
0.31 | 2012.889 | 290.083 |  |  |  | 0.31 | 2012.889 | 314.543
0.315 | 1927.447 | 303.319 |  |  |  | 0.315 | 1927.447 | 298.849
0.32 | 1842.006 | 300.152 |  |  |  | 0.32 | 1842.006 | 296.532
0.325 | 2269.213 | 318.325 |  |  |  | 0.325 | 1703.983 | 325.832
0.33 | 1884.726 | 308.457 |  |  |  | 0.33 | 1884.726 | 308.934
0.335 | 1799.285 | 337.689 |  |  |  | 0.335 | 1799.285 | 312.272
0.34 | 1970.168 | 284.406 |  |  |  | 0.34 | 1970.168 | 308.254
0.345 | 1970.168 | 302.678 |  |  |  | 0.345 | 1970.168 | 295.622
0.35 | 1927.447 | 298.436 |  |  |  | 0.35 | 1927.447 | 292.7
0.355 | 2055.609 | 297.106 |  |  |  | 0.355 | 2055.609 | 295.104
0.36 | 1884.726 | 325.807 |  |  |  | 0.36 | 1884.726 | 304.833
0.365 | 1756.564 | 311.628 |  |  |  | 0.365 | 1756.564 | 302.161
0.37 | 1970.168 | 296.046 |  |  |  | 0.37 | 1970.168 | 299.144
0.375 | 1927.447 | 303.115 |  |  |  | 0.375 | 1927.447 | 301.683
0.38 | 1970.168 | 303.501 |  |  |  | 0.38 | 1970.168 | 301.148
0.385 | 2012.889 | 294.116 |  |  |  | 0.385 | 2012.889 | 287.216
0.39 | 2354.655 | 266.061 |  |  |  | 0.39 | 2354.655 | 262.642
0.395 | 2610.979 | 238.961 |  |  |  | 0.395 | 2610.979 | 242.992
0.4 | 2482.817 | 241.726 |  |  |  | 0.4 | 2482.817 | 239.327
0.405 | 2525.538 | 248.26 |  |  |  | 0.405 | 2525.538 | 249.228
0.41 | 2183.772 | 287.391 |  |  |  | 0.41 | 2183.772 | 284.325
0.415 | 1842.006 | 325.373 |  |  |  | 0.415 | 1842.006 | 312.383
0.42 | 2354.655 | 304.297 |  |  |  | 0.42 | 2354.655 | 311.324
0.425 | 2098.33 | 254.913 |  |  |  | 0.425 | 2098.33 | 291.295
0.43 | 1884.726 | 304.396 |  |  |  | 0.43 | 1884.726 | 286.167
0.435 | 1884.726 | 298.294 |  |  |  | 0.435 | 1884.726 | 291.755
0.44 | 2183.772 | 289.834 |  |  |  | 0.44 | 2183.772 | 293.532
0.445 | 2098.33 | 306.117 |  |  |  | 0.445 | 2098.33 | 308.081
0.45 | 1884.726 | 288.884 |  |  |  | 0.45 | 1884.726 | 296.074
0.455 | 2440.096 | 256.731 |  |  |  | 0.455 | 2440.096 | 268.043
0.46 | 2525.538 | 242.57 |  |  |  | 0.46 | 2525.538 | 239.054
0.465 | 2482.817 | 244.977 |  |  |  | 0.465 | 2482.817 | 244.903
0.47 | 2397.375 | 254.109 |  |  |  | 0.47 | 2397.375 | 250.657
0.475 | 2397.375 | 248.67 |  |  |  | 0.475 | 2397.375 | 254.962
0.48 | 2354.655 | 257.215 |  |  |  | 0.48 | 2354.655 | 252.203
0.485 | 2525.538 | 251.716 |  |  |  | 0.485 | 2525.538 | 249.561
0.49 | 2397.375 | 252.609 |  |  |  | 0.49 | 2397.375 | 257.308
0.495 | 2354.655 | 262.035 |  |  |  | 0.495 | 2354.655 | 264.869
0.5 | 2311.934 | 248.471 |  |  |  | 0.5 | 2311.934 | 262.375
0.505 | 2311.934 | 258.808 |  |  |  | 0.505 | 2311.934 | 253.998
0.51 | 2354.655 | 254.78 |  |  |  | 0.51 | 2354.655 | 253.022
0.515 | 2397.375 | 253.785 |  |  |  | 0.515 | 2397.375 | 251.116
0.52 | 2482.817 | 254.985 |  |  |  | 0.52 | 2482.817 | 247.932
0.525 | 2226.492 | 267.271 |  |  |  | 0.525 | 2226.492 | 270.177
0.53 | 2269.213 | 276.096 |  |  |  | 0.53 | 2269.213 | 278.462
0.535 | 1884.726 | 305.789 |  |  |  | 0.535 | 1884.726 | 300.165
0.54 | 2183.772 | 277.133 |  |  |  | 0.54 | 2183.772 | 277.831
0.545 | 2098.33 | 284.318 |  |  |  | 0.545 | 2098.33 | 285.28
0.55 | 1970.168 | 303.382 |  |  |  | 0.55 | 1970.168 | 298.937
0.555 | 1756.564 | 302.896 |  |  |  | 0.555 | 1756.564 | 296.844
0.56 | 2012.889 | 289.884 |  |  |  | 0.56 | 2012.889 | 289.697
0.565 | 1884.726 | 296.374 |  |  |  | 0.565 | 1884.726 | 290.34
0.57 | 2183.772 | 287.091 |  |  |  | 0.57 | 2183.772 | 282.243
0.575 | 1884.726 | 308.178 |  |  |  | 0.575 | 1884.726 | 312.243
0.58 | 1713.843 | 313.769 |  |  |  | 0.58 | 1713.843 | 318.476
0.585 | 1628.402 | 316.695 |  |  |  | 0.585 | 1628.402 | 321.282
0.59 | 1799.285 | 323.995 |  |  |  | 0.59 | 1799.285 | 323.501
0.595 | 1628.402 | 332.765 |  |  |  | 0.595 | 1628.402 | 329.95
0.6 | 1842.006 | 310.787 |  |  |  | 0.6 | 1842.006 | 320.918
0.605 | 2098.33 | 297.935 |  |  |  | 0.605 | 2098.33 | 306.232
0.61 | 2428.622 | 257.241 |  |  |  | 0.61 | 2428.622 | 269.849
0.614 | 2739.142 | 230.586 |  |  |  | 0.614 | 2739.142 | 215.519
0.617 | 3319.715 | 177.497 |  |  |  | 0.617 | 3319.715 | 200.132
0.62 | 2824.583 | 219.284 |  |  |  | 0.62 | 2824.583 | 212.322
0.625 | 2482.817 | 243.604 |  |  |  | 0.625 | 2482.817 | 242.747
0.63 | 2482.817 | 249.729 |  |  |  | 0.63 | 2482.817 | 249.189
0.635 | 2440.096 | 259.331 |  |  |  | 0.635 | 2440.096 | 249.319
0.64 | 2311.934 | 263.677 |  |  |  | 0.64 | 2311.934 | 253.692
0.645 | 2525.538 | 229.589 |  |  |  | 0.645 | 2525.538 | 250.047
0.65 | 2397.375 | 264.297 |  |  |  | 0.65 | 2397.375 | 258.928
0.655 | 2311.934 | 267.562 |  |  |  | 0.655 | 2311.934 | 264.227
0.66 | 2440.096 | 261.827 |  |  |  | 0.66 | 2440.096 | 260.509
0.665 | 2354.655 | 263.322 |  |  |  | 0.665 | 2354.655 | 262.44
0.67 | 2311.934 | 268.412 |  |  |  | 0.67 | 2311.934 | 267.008
0.675 | 2226.492 | 273.068 |  |  |  | 0.675 | 2226.492 | 272.042
0.68 | 2141.051 | 276.205 |  |  |  | 0.68 | 2141.051 | 275.136
0.685 | 2141.051 | 286.183 |  |  |  | 0.685 | 2141.051 | 286.235
0.69 | 1884.726 | 310.231 |  |  |  | 0.69 | 1884.726 | 313.94
0.695 | 1842.006 | 321.137 |  |  |  | 0.695 | 1842.006 | 318.734
0.7 | 1756.564 | 313.606 |  |  |  | 0.7 | 1815.18 | 309.294
0.705 | 1756.564 | 312.768 |  |  |  | 0.705 | 1815.18 | 311.767
0.71 | 1756.564 | 319.785 |  |  |  | 0.71 | 1783.409 | 319.619
0.715 | 1628.402 | 328.014 |  |  |  | 0.715 | 1688.098 | 327.538
0.72 | 1842.006 | 305.4 |  |  |  | 0.72 | 1942.263 | 299.135
0.725 | 1970.168 | 283.078 |  |  |  | 0.725 | 2418.823 | 264.545
0.728 | 2701.544 | 226.854 |  |  |  | 0.73 | 3087.721 | 210.273
0.73 | 3465.394 | 150.538 |  |  |  | 0.735 | 3337.232 | 163.971
0.735 | 3337.232 | 160.256 |  |  |  | 0.74 | 2857.747 | 206.339
0.74 | 3550.836 | 189.442 |  |  |  | 0.741 | 2878.164 | 218.066
0.741 | 2878.164 | 234.313 |  |  |  | 0.745 | 2397.375 | 268.155
0.745 | 2397.375 | 263.467 |  |  |  | 0.75 | 2269.213 | 274.253
0.75 | 2269.213 | 271.451 |  |  |  | 0.755 | 2141.051 | 292.396
0.755 | 2141.051 | 288.184 |  |  |  | 0.76 | 1756.564 | 302.169
0.76 | 1756.564 | 310.24 |  |  |  | 0.765 | 1970.168 | 295.505
0.765 | 1970.168 | 298.701 |  |  |  | 0.77 | 2012.889 | 300.624
0.77 | 2012.889 | 296.478 |  |  |  | 0.775 | 2012.889 | 292.983
0.775 | 2012.889 | 293.763 |  |  |  | 0.78 | 2141.051 | 279.486
0.78 | 2141.051 | 277.731 |  |  |  | 0.785 | 2183.772 | 282.549
0.785 | 2183.772 | 284.127 |  |  |  | 0.79 | 2012.889 | 303.446
0.79 | 2012.889 | 302.451 |  |  |  | 0.795 | 1842.006 | 308.881
0.795 | 1842.006 | 312.009 |  |  |  | 0.8 | 1970.168 | 302.38
0.8 | 1970.168 | 305.823 |  |  |  | 0.805 | 1970.168 | 304.603
0.805 | 1970.168 | 304.232 |  |  |  | 0.81 | 2055.609 | 302.967
0.81 | 2055.609 | 300.82 |  |  |  | 0.815 | 2098.33 | 300.933
0.815 | 2098.33 | 298.707 |  |  |  | 0.82 | 2012.889 | 297.32
0.82 | 2012.889 | 298.657 |  |  |  | 0.825 | 1927.447 | 322.711
0.825 | 1927.447 | 308.595 |  |  |  | 0.83 | 1884.726 | 327.341
0.83 | 1884.726 | 315.631 |  |  |  | 0.835 | 1842.006 | 320.973
0.835 | 1842.006 | 323.349 |  |  |  | 0.84 | 1998.546 | 307.691
0.84 | 1998.546 | 308.315 |  |  |  | 0.845 | 2055.609 | 291.304
0.845 | 2055.609 | 294.962 |  |  |  | 0.85 | 1842.006 | 300.34
0.85 | 1842.006 | 302.601 |  |  |  | 0.855 | 2183.772 | 287.358
0.855 | 2183.772 | 285.934 |  |  |  | 0.86 | 2098.33 | 280.497
0.86 | 2098.33 | 285.453 |  |  |  | 0.865 | 2226.492 | 268.81
0.865 | 2226.492 | 268.149 |  |  |  | 0.87 | 2482.817 | 251.852
0.87 | 2482.817 | 250.236 |  |  |  | 0.875 | 2397.375 | 256.233
0.875 | 2397.375 | 257.43 |  |  |  | 0.88 | 2387.052 | 254.414
0.88 | 2397.375 | 257.591 |  |  |  | 0.885 | 2418.822 | 249.705
0.885 | 2440.096 | 250.346 |  |  |  | 0.89 | 2418.822 | 243.839
0.89 | 2397.375 | 247.315 |  |  |  | 0.895 | 3149.292 | 203.576
0.895 | 3149.292 | 174.746 |  |  |  | 0.9 | 2653.7 | 225.992
0.9 | 2653.7 | 226.245 |  |  |  | 0.905 | 2568.258 | 240.877
0.905 | 2568.258 | 242.703 |  |  |  | 0.91 | 2440.096 | 250.153
0.91 | 2440.096 | 250.56 |  |  |  | 0.915 | 2397.375 | 258.002
0.915 | 2397.375 | 256.229 |  |  |  | 0.92 | 2311.934 | 264.154
0.92 | 2311.934 | 262.804 |  |  |  | 0.925 | 2269.213 | 275.726
0.925 | 2269.213 | 274.474 |  |  |  | 0.93 | 2311.934 | 271.617
0.93 | 2311.934 | 269.206 |  |  |  | 0.935 | 2440.096 | 252.603
0.935 | 2440.096 | 252.837 |  |  |  | 0.94 | 2525.538 | 242.788
0.94 | 2525.538 | 244.036 |  |  |  | 0.945 | 2545.905 | 240.71
0.945 | 2568.258 | 242.228 |  |  |  | 0.95 | 2482.364 | 244.113
0.95 | 2482.817 | 244.85 |  |  |  | 0.955 | 2482.364 | 239.561
0.955 | 2482.817 | 244.949 |  |  |  | 0.96 | 2545.905 | 237.67
0.96 | 2568.258 | 239.502 |  |  |  | 0.965 | 2418.822 | 245.517
0.965 | 2440.096 | 243.946 |  |  |  | 0.97 | 2482.364 | 249.217
0.97 | 2482.817 | 252.768 |  |  |  | 0.975 | 2482.364 | 243.968
0.975 | 2440.096 | 243.017 |  |  |  | 0.98 | 2482.364 | 250.975
0.98 | 2440.096 | 250.678 |  |  |  | 0.985 | 2387.052 | 265.779
0.985 | 2397.375 | 262.925 |  |  |  | 0.99 | 1942.263 | 301.118
0.99 | 1970.168 | 301.104 |  |  |  | 0.995 | 1910.492 | 313.281
0.995 | 1884.726 | 311.31 |  |  |  | 1 | 1783.409 | 307.321
1 | 1799.285 | 312.849 |  |  |  | 1.005 | 2005.804 | 303.039
1.005 | 1884.726 | 295.626 |  |  |  | 1.01 | 1783.41 | 323.777
1.01 | 1394.718 | 357.785 |  |  |  | 1.014 | 2104.067 | 307.344
1.014 | 2104.067 | 294.736 |  |  |  | 1.02 | 1927.447 | 275.579
1.02 | 1927.447 | 274.352 |  |  |  | 1.025 | 2055.609 | 288.03
1.025 | 2055.609 | 292.892 |  |  |  | 1.03 | 2005.804 | 289.251
1.03 | 1970.168 | 294.895 |  |  |  | 1.035 | 2228.199 | 268.72
1.035 | 2269.213 | 271.884 |  |  |  | 1.04 | 2387.052 | 256.423
1.04 | 2397.375 | 257.618 |  |  |  | 1.045 | 2609.446 | 231.879
1.045 | 2397.375 | 228.726 |  |  |  | 1.05 | 2958.924 | 203.114
1.05 | 2952.745 | 199.757 |  |  |  | 1.055 | 2863.612 | 205.717
1.055 | 2824.583 | 206.353 |  |  |  | 1.06 | 2831.841 | 207.398
1.06 | 2824.583 | 207.122 |  |  |  | 1.065 | 2990.694 | 200.846
1.065 | 2867.304 | 201.446 |  |  |  | 1.07 | 3054.235 | 190.498
1.07 | 3038.187 | 191.203 |  |  |  | 1.075 | 3181.318 | 182.607
1.075 | 3166.349 | 180.742 |  |  |  | 1.08 | 3117.777 | 182.942
1.08 | 3123.628 | 182.852 |  |  |  | 1.085 | 3086.006 | 185.121
1.085 | 3080.908 | 185.845 |  |  |  | 1.09 | 3022.465 | 188.434
1.09 | 3080.908 | 189.151 |  |  |  | 1.095 | 3086.006 | 192.101
1.095 | 3080.908 | 192.598 |  |  |  | 1.1 | 2990.694 | 190.723
1.1 | 2995.466 | 191.29 |  |  |  | 1.105 | 3149.547 | 190.26
1.105 | 3166.349 | 188.963 |  |  |  | 1.11 | 2593.561 | 191.545
1.11 | 2995.466 | 191.587 |  |  |  | 1.115 | 1433.932 | 157.294
1.113 | 1995.064 | 194.247
1.114 | 758.723 | 192.954

## Test-2195
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2195
Scenario | 480V - 5kA Available Arc on battery side of breaker with Cabinet A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 434.9
Arc Current (A) | 3124
Arc Voltage (V) | 170.8
Duration of Arc (s) | 1.014
Arc Energy (kJ) | 518.2 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 1.52 |  | Test 23-2195 was taken inside of the battery cabinet at highest voltage and lowest current. Connections were made to the other side of the circuit breaker by rotating the circuit breaker 180°. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A significant blast and black smoke were observed, followed by continuous arcing and eventually a fire near the terminals of the circuit breaker. Review of high-speed video shows arcing, followed by a fire exhausting from the opening of the battery cabinet. It was decided to proceed with the next test at a higher current level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 4.09
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 3326.133 | 47.456 |  |  |  | 0.11 | 3567.566 | 108.079
0.12 | 2900.08 | 156.271 |  |  |  | 0.12 | 3820.216 | 168.732
0.13 | 2942.685 | 197.007 |  |  |  | 0.13 | 2904.358 | 192.651
0.14 | 2857.474 | 196.281 |  |  |  | 0.14 | 2872.777 | 195.822
0.15 | 2942.685 | 191.089 |  |  |  | 0.15 | 2999.102 | 173.642
0.16 | 4263.451 | 144.319 |  |  |  | 0.16 | 3520.194 | 142.129
0.17 | 4050.424 | 87.542 |  |  |  | 0.17 | 4041.285 | 87.588
0.18 | 4050.424 | 87.511 |  |  |  | 0.18 | 4009.704 | 89.659
0.19 | 3922.608 | 91.781 |  |  |  | 0.19 | 3946.541 | 94.167
0.2 | 3922.608 | 97.348 |  |  |  | 0.2 | 3914.96 | 99.387
0.21 | 3880.003 | 102.078 |  |  |  | 0.21 | 3851.798 | 104.539
0.22 | 3837.397 | 105.902 |  |  |  | 0.22 | 3820.216 | 107.156
0.23 | 3880.003 | 105.547 |  |  |  | 0.23 | 3851.798 | 106.348
0.24 | 3837.397 | 105.068 |  |  |  | 0.24 | 3820.216 | 106.715
0.25 | 3794.792 | 108.163 |  |  |  | 0.25 | 3788.635 | 110.125
0.26 | 3794.792 | 111.555 |  |  |  | 0.26 | 3757.054 | 112.792
0.27 | 3794.792 | 112.311 |  |  |  | 0.27 | 3788.635 | 113.212
0.28 | 3794.792 | 111.96 |  |  |  | 0.28 | 3757.054 | 113.194
0.29 | 3752.187 | 113.203 |  |  |  | 0.29 | 3788.635 | 114.32
0.3 | 3709.581 | 114.341 |  |  |  | 0.3 | 3725.472 | 115.314
0.31 | 3752.187 | 114.234 |  |  |  | 0.31 | 3725.472 | 115.173
0.32 | 3709.581 | 114.604 |  |  |  | 0.32 | 3725.472 | 115.693
0.33 | 3752.187 | 114.185 |  |  |  | 0.33 | 3725.472 | 115.775
0.34 | 3752.187 | 115.069 |  |  |  | 0.34 | 3725.472 | 117.078
0.35 | 3709.581 | 117.865 |  |  |  | 0.35 | 3693.891 | 120.472
0.36 | 3666.976 | 120.148 |  |  |  | 0.36 | 3662.31 | 122.08
0.37 | 3709.581 | 121.875 |  |  |  | 0.37 | 3662.31 | 123.458
0.38 | 3666.976 | 123.525 |  |  |  | 0.38 | 3630.728 | 126.042
0.39 | 3624.371 | 126.835 |  |  |  | 0.39 | 3599.147 | 128.758
0.4 | 3539.16 | 130.265 |  |  |  | 0.4 | 3567.566 | 131.581
0.41 | 3539.16 | 133.257 |  |  |  | 0.41 | 3535.984 | 134.815
0.42 | 3539.16 | 135.175 |  |  |  | 0.42 | 3504.403 | 135.652
0.43 | 3539.16 | 134.497 |  |  |  | 0.43 | 3535.984 | 135.404
0.44 | 3539.16 | 136.461 |  |  |  | 0.44 | 3504.403 | 137.591
0.45 | 3453.949 | 137.431 |  |  |  | 0.45 | 3441.24 | 138.74
0.46 | 3539.16 | 136.761 |  |  |  | 0.46 | 3504.403 | 138.568
0.47 | 3453.949 | 140.318 |  |  |  | 0.47 | 3441.24 | 141.666
0.48 | 3453.949 | 144.116 |  |  |  | 0.48 | 3409.659 | 144.943
0.49 | 3453.949 | 145.114 |  |  |  | 0.49 | 3409.659 | 146.334
0.5 | 3368.738 | 147.294 |  |  |  | 0.5 | 3378.078 | 148.14
0.51 | 3368.738 | 147.064 |  |  |  | 0.51 | 3346.497 | 147.025
0.52 | 3496.555 | 145.652 |  |  |  | 0.52 | 3472.822 | 144.734
0.53 | 3496.555 | 144.389 |  |  |  | 0.53 | 3472.822 | 146.769
0.54 | 3326.133 | 150.599 |  |  |  | 0.54 | 3378.078 | 153.456
0.55 | 3283.528 | 159.235 |  |  |  | 0.55 | 3251.753 | 162.484
0.56 | 3198.317 | 165.14 |  |  |  | 0.56 | 3220.171 | 166.058
0.57 | 3240.922 | 164.572 |  |  |  | 0.57 | 3220.171 | 164.61
0.58 | 3198.317 | 164.783 |  |  |  | 0.58 | 3188.59 | 166.257
0.59 | 3155.712 | 171.974 |  |  |  | 0.59 | 3125.427 | 173.713
0.6 | 3070.501 | 175.568 |  |  |  | 0.6 | 3062.265 | 175.203
0.61 | 3113.106 | 170.117 |  |  |  | 0.61 | 3125.427 | 168.337
0.62 | 3368.738 | 157.79 |  |  |  | 0.62 | 3314.915 | 160.264
0.63 | 3283.528 | 157.936 |  |  |  | 0.63 | 3283.334 | 162.522
0.64 | 3113.106 | 174.028 |  |  |  | 0.64 | 3093.846 | 176.828
0.65 | 2942.685 | 183.448 |  |  |  | 0.65 | 2967.521 | 183.916
0.66 | 3027.896 | 185.054 |  |  |  | 0.66 | 3030.683 | 184.931
0.67 | 3027.896 | 188.467 |  |  |  | 0.67 | 2935.94 | 189.938
0.68 | 2900.08 | 193.539 |  |  |  | 0.68 | 2904.358 | 188.634
0.69 | 3198.317 | 171.862 |  |  |  | 0.69 | 3125.427 | 178.314
0.7 | 2942.685 | 194.009 |  |  |  | 0.7 | 2999.102 | 189.269
0.71 | 2814.869 | 197.54 |  |  |  | 0.71 | 2872.777 | 190.668
0.72 | 3198.317 | 180.769 |  |  |  | 0.72 | 3157.009 | 180.951
0.73 | 3070.501 | 179.422 |  |  |  | 0.73 | 3062.265 | 181.645
0.74 | 3027.896 | 182.369 |  |  |  | 0.74 | 3062.265 | 185.423
0.75 | 2942.685 | 188.318 |  |  |  | 0.75 | 2904.358 | 194.235
0.76 | 2772.264 | 204.22 |  |  |  | 0.76 | 2809.614 | 207.238
0.77 | 2687.053 | 207.662 |  |  |  | 0.77 | 2714.87 | 207.791
0.78 | 2857.474 | 204.152 |  |  |  | 0.78 | 2809.614 | 203.439
0.79 | 2729.658 | 201.467 |  |  |  | 0.79 | 2778.033 | 201.167
0.8 | 2857.474 | 198.192 |  |  |  | 0.8 | 2872.777 | 196.79
0.81 | 2985.29 | 195.113 |  |  |  | 0.81 | 2935.94 | 196.737
0.82 | 2942.685 | 199.571 |  |  |  | 0.82 | 2904.358 | 203.174
0.83 | 2729.658 | 212.326 |  |  |  | 0.83 | 2683.289 | 209.225
0.84 | 2857.474 | 207.433 |  |  |  | 0.84 | 2841.196 | 211.516
0.85 | 2644.447 | 212.058 |  |  |  | 0.85 | 2683.289 | 211.359
0.86 | 2729.658 | 209.808 |  |  |  | 0.86 | 2778.033 | 206.904
0.87 | 2985.29 | 198.224 |  |  |  | 0.87 | 2904.358 | 201.701
0.88 | 2814.869 | 199.074 |  |  |  | 0.88 | 2809.614 | 201.078
0.89 | 2900.08 | 204.4 |  |  |  | 0.89 | 2904.358 | 206.778
0.9 | 2601.842 | 216.79 |  |  |  | 0.9 | 2620.126 | 217.009
0.91 | 2857.474 | 207.524 |  |  |  | 0.91 | 2746.452 | 209.872
0.92 | 3049.199 | 199.335 |  |  |  | 0.92 | 3046.474 | 185.435
0.93 | 2729.658 | 214.33 |  |  |  | 0.93 | 2967.521 | 205.477
0.94 | 2559.237 | 226.858 |  |  |  | 0.94 | 2556.964 | 232.516
0.95 | 2474.026 | 231.499 |  |  |  | 0.95 | 2651.708 | 209.371
0.96 | 2729.658 | 214.253 |  |  |  | 0.96 | 2778.033 | 212.13
0.97 | 2388.815 | 234.852 |  |  |  | 0.97 | 2399.057 | 243.843
0.98 | 2474.026 | 237.142 |  |  |  | 0.98 | 2493.801 | 236.167
0.99 | 2516.631 | 235.943 |  |  |  | 0.99 | 2493.801 | 237.126
1 | 2388.815 | 240.644 |  |  |  | 1 | 2399.057 | 239.964
1.01 | 2516.631 | 243.349 |  |  |  | 1.01 | 2493.801 | 241.76
1.02 | 2388.815 | 247.209 |  |  |  | 1.02 | 2335.895 | 249.392
1.03 | 2218.394 | 248.591 |  |  |  | 1.03 | 2367.476 | 244.624
1.04 | 2516.631 | 235.697 |  |  |  | 1.04 | 2525.382 | 235.28
1.05 | 2516.631 | 229.106 |  |  |  | 1.05 | 2525.382 | 220.652
1.06 | 3326.133 | 208.197 |  |  |  | 1.06 | 3378.078 | 216.152
1.07 | 2431.421 | 237.446 |  |  |  | 1.07 | 2430.639 | 230.929
1.08 | 2431.421 | 226.216 |  |  |  | 1.08 | 2651.708 | 224.505
1.09 | 2942.685 | 186.453 |  |  |  | 1.09 | 2999.102 | 185.363
1.1 | 2900.08 | 193.614 |  |  |  | 1.1 | 2967.521 | 201.57
1.11 | 2687.053 | 217.452 |  |  |  | 1.11 | 2588.545 | 232.443
1.12 | 2175.789 | 266.751 |  |  |  | 1.12 | 1783.222 | 340.186
2.28 | 1792.341 | 259.957 |  |  |  | 1.13 | 2556.964 | 416.142
2.29 | 2772.264 | 192.395 |  |  |  | 2.28 | 2493.801 | 335.729
2.3 | 2772.264 | 211.692 |  |  |  | 2.29 | 2778.033 | 258.048
2.31 | 2601.842 | 224.361 |  |  |  | 2.3 | 2746.452 | 213.522
2.32 | 2431.421 | 238.248 |  |  |  | 2.31 | 2556.964 | 230.126
2.33 | 2346.21 | 249.514 |  |  |  | 2.32 | 2462.22 | 242.738
2.34 | 2260.999 | 254.756 |  |  |  | 2.33 | 2335.895 | 252.485
2.35 | 2260.999 | 256.994 |  |  |  | 2.34 | 2272.732 | 258.225
2.36 | 2218.394 | 259.196 |  |  |  | 2.35 | 2272.732 | 261.048
2.37 | 2218.394 | 258.854 |  |  |  | 2.36 | 2209.569 | 261.039
2.38 | 2260.999 | 255.556 |  |  |  | 2.37 | 2209.569 | 258.136
2.39 | 2303.605 | 251.293 |  |  |  | 2.38 | 2241.151 | 252.669
2.4 | 2175.789 | 253.179 |  |  |  | 2.39 | 2304.313 | 245.116
2.41 | 2218.394 | 257.629 |  |  |  | 2.4 | 2209.569 | 252.54
2.42 | 2346.21 | 245.799 |  |  |  | 2.41 | 2209.569 | 257.576
2.43 | 2260.999 | 247.013 |  |  |  | 2.42 | 2335.895 | 238.609
2.44 | 2303.605 | 275.87 |  |  |  | 2.43 | 2304.313 | 244.153
2.45 | 2516.631 | 194.798 |  |  |  | 2.44 | 2620.126 | 268.607
2.46 | 1494.103 | 335.178 |  |  |  | 2.45 | 2272.732 | 246.458
2.47 | 2346.21 | 249.378 |  |  |  | 2.46 | 1609.525 | 313.718
2.48 | 2388.815 | 253.501 |  |  |  | 2.47 | 2478.011 | 253.338
2.49 | 2133.183 | 263.326 |  |  |  | 2.48 | 2367.476 | 255.646
2.5 | 2260.999 | 258.854 |  |  |  | 2.49 | 2209.569 | 261.473
2.51 | 2218.394 | 258.202 |  |  |  | 2.5 | 2304.313 | 257.359
2.52 | 2218.394 | 262.01 |  |  |  | 2.51 | 2146.407 | 258.842
2.53 | 2133.183 | 304.148 |  |  |  | 2.52 | 2209.569 | 258.43
3.876 | 1341.27 | 369.824 |  |  |  | 2.53 | 2620.126 | 345.028
3.88 | 2516.631 | 294.324 |  |  |  | 2.54 | 2241.151 | 414.074
3.89 | 2090.578 | 303.822 |  |  |  | 3.88 | 2430.639 | 317.988
3.9 | 2793.567 | 255.546 |  |  |  | 3.89 | 2399.058 | 289.506
3.905 | 857.873 | 391.277 |  |  |  | 3.9 | 2809.614 | 314.489

## Test-2196
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2196
Scenario | 480V - 20kA Available Arc on battery side of breaker with Cabinet A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 6894
Arc Current (A) | 434.9
Arc Voltage (V) | 341.1
Duration of Arc (s) | 0.3115
Arc Energy (kJ) | 641.4 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 2.3 |  | Test 23-2196 was taken inside of the battery cabinet at highest voltage and highest current. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A significant blast, arcing, and black smoke were observed, followed by a fire near the terminals of the circuit breaker. As a result, the circuit breaker could no longer be used. Review of high speed video shows the arc grow towards the calorimeter placed in front of the battery cabinet, before growing further and extending just below it. Nonetheless, it was decided to proceed with the next test at a lower current level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 20000 | 0 | Incident Energy at 6" distance (cal/cm²) | 2.98
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 5491.519 | 55.896 |  |  |  | 0.11 | 6122.354 | 93.151
0.111 | 10146.252 | 128.57 |  |  |  | 0.112 | 11067.914 | 197.158
0.112 | 12447.061 | 189.501 |  |  |  | 0.116 | 11487.23 | 255.388
0.114 | 12532.159 | 236.709 |  |  |  | 0.118 | 10791.006 | 272.92
0.116 | 11745.003 | 262.779 |  |  |  | 0.12 | 10221.368 | 278.357
0.118 | 10489.807 | 270.291 |  |  |  | 0.122 | 10063.135 | 282.505
0.12 | 10191.964 | 276.23 |  |  |  | 0.124 | 9683.376 | 286.479
0.122 | 10085.591 | 280.752 |  |  |  | 0.126 | 9208.677 | 291.698
0.124 | 10021.768 | 283.826 |  |  |  | 0.128 | 9208.677 | 295.781
0.126 | 9553.729 | 289.317 |  |  |  | 0.13 | 9271.971 | 299.383
0.128 | 9085.69 | 293.221 |  |  |  | 0.132 | 8987.151 | 299.2
0.13 | 9426.082 | 297.1 |  |  |  | 0.134 | 8765.625 | 299.206
0.132 | 9213.337 | 296.315 |  |  |  | 0.136 | 8828.919 | 301.469
0.134 | 8958.044 | 296.285 |  |  |  | 0.138 | 8955.505 | 303.877
0.136 | 8787.848 | 298.495 |  |  |  | 0.14 | 8860.565 | 305.078
0.138 | 9043.141 | 300.883 |  |  |  | 0.142 | 8575.746 | 304.236
0.14 | 8872.946 | 301.958 |  |  |  | 0.144 | 8607.393 | 304.229
0.142 | 8362.358 | 301.24 |  |  |  | 0.146 | 8797.272 | 304.353
0.144 | 8575.103 | 301.151 |  |  |  | 0.148 | 8797.272 | 304.468
0.146 | 8915.495 | 300.812 |  |  |  | 0.15 | 8575.746 | 307.318
0.148 | 8872.946 | 300.818 |  |  |  | 0.152 | 8385.867 | 310.452
0.15 | 8532.554 | 303.575 |  |  |  | 0.154 | 8512.453 | 310.031
0.152 | 8490.005 | 306.252 |  |  |  | 0.156 | 8639.039 | 308.962
0.154 | 8660.201 | 305.922 |  |  |  | 0.158 | 8385.867 | 308.505
0.156 | 8575.103 | 305.399 |  |  |  | 0.16 | 8290.927 | 308.377
0.158 | 8447.456 | 305.582 |  |  |  | 0.162 | 8480.806 | 306.316
0.16 | 8447.456 | 305.537 |  |  |  | 0.164 | 8828.919 | 297.339
0.162 | 8575.103 | 303.907 |  |  |  | 0.166 | 9082.091 | 287.714
0.164 | 8660.201 | 294.107 |  |  |  | 0.168 | 9145.384 | 293.037
0.166 | 9128.239 | 283.517 |  |  |  | 0.17 | 9113.738 | 293.06
0.168 | 9255.886 | 293.091 |  |  |  | 0.172 | 9335.264 | 284.813
0.17 | 8958.044 | 294.518 |  |  |  | 0.174 | 9778.316 | 278.133
0.172 | 9553.729 | 285.471 |  |  |  | 0.176 | 9715.023 | 291.228
0.174 | 9979.219 | 268.894 |  |  |  | 0.178 | 9398.557 | 292.975
0.176 | 9766.474 | 283.801 |  |  |  | 0.18 | 9620.083 | 287.226
0.178 | 9553.729 | 289.161 |  |  |  | 0.182 | 9778.316 | 284.056
0.18 | 9660.102 | 282.347 |  |  |  | 0.184 | 9683.376 | 290.618
0.182 | 9830.297 | 277.21 |  |  |  | 0.186 | 9208.677 | 306.063
0.184 | 9426.082 | 286.904 |  |  |  | 0.188 | 8670.686 | 319.675
0.186 | 9149.514 | 301.412 |  |  |  | 0.19 | 8101.047 | 327.644
0.188 | 8872.946 | 318.054 |  |  |  | 0.192 | 7531.409 | 328.632
0.19 | 8149.613 | 325.265 |  |  |  | 0.194 | 7468.116 | 328.576
0.192 | 7341.182 | 325.425 |  |  |  | 0.196 | 7594.702 | 327.859
0.194 | 7468.829 | 326.065 |  |  |  | 0.198 | 7626.349 | 328.391
0.196 | 7681.574 | 325.651 |  |  |  | 0.2 | 7373.176 | 331.427
0.198 | 7639.025 | 325.966 |  |  |  | 0.202 | 7214.943 | 333.203
0.2 | 7277.359 | 328.439 |  |  |  | 0.204 | 7341.53 | 332.601
0.202 | 7256.084 | 329.911 |  |  |  | 0.206 | 7341.53 | 332.123
0.204 | 7553.927 | 329.499 |  |  |  | 0.208 | 7214.943 | 330.598
0.206 | 7341.182 | 329.484 |  |  |  | 0.21 | 7278.237 | 326.242
0.208 | 7085.888 | 327.218 |  |  |  | 0.212 | 7563.056 | 319.057
0.21 | 7383.731 | 323.953 |  |  |  | 0.214 | 8037.754 | 296.176
0.212 | 7660.3 | 318.694 |  |  |  | 0.216 | 9177.031 | 267.848
0.214 | 7936.868 | 303.928 |  |  |  | 0.218 | 10522.01 | 238.18
0.216 | 9043.142 | 261.946 |  |  |  | 0.22 | 12215.102 | 223.353
0.218 | 10255.788 | 243.79 |  |  |  | 0.222 | 12658.154 | 232.477
0.22 | 12106.669 | 205.555 |  |  |  | 0.224 | 12025.222 | 242.489
0.222 | 12808.727 | 230.148 |  |  |  | 0.226 | 11613.817 | 248.385
0.224 | 12361.963 | 240.225 |  |  |  | 0.228 | 11392.291 | 261.886
0.226 | 11468.434 | 245.536 |  |  |  | 0.23 | 10885.946 | 280.817
0.228 | 11340.787 | 254.29 |  |  |  | 0.232 | 9809.962 | 289.552
0.23 | 11191.865 | 276.064 |  |  |  | 0.234 | 9525.143 | 295.589
0.232 | 10149.415 | 286.061 |  |  |  | 0.236 | 9082.091 | 301.153
0.234 | 9213.337 | 291.538 |  |  |  | 0.238 | 9018.798 | 301.744
0.236 | 9383.533 | 298.247 |  |  |  | 0.24 | 9018.798 | 273.218
0.238 | 9128.239 | 299.412 |  |  |  | 0.242 | 10332.131 | 248.481
0.24 | 9043.141 | 296.711 |  |  |  | 0.244 | 11645.464 | 223.959
0.242 | 9213.337 | 231.935 |  |  |  | 0.246 | 12404.981 | 230.016
0.243 | 10462.053 | 215.934 |  |  |  | 0.248 | 12499.921 | 231.939
0.244 | 11766.277 | 216.738 |  |  |  | 0.25 | 12278.395 | 223.555
0.246 | 12638.531 | 226.092 |  |  |  | 0.252 | 12499.921 | 220.774
0.248 | 12361.963 | 229.414 |  |  |  | 0.254 | 12816.387 | 232.654
0.25 | 12276.865 | 220.341 |  |  |  | 0.256 | 12499.921 | 251.401
0.252 | 12723.629 | 216.18 |  |  |  | 0.258 | 11392.291 | 272.897
0.254 | 12808.727 | 226.885 |  |  |  | 0.26 | 10063.135 | 304.698
0.256 | 12468.336 | 247.39 |  |  |  | 0.262 | 8844.742 | 349.053
0.258 | 11482.617 | 266.35 |  |  |  | 0.264 | 7067.259 | 381.549
0.26 | 10277.062 | 295.012 |  |  |  | 0.266 | 5537.675 | 374.37
0.262 | 8724.024 | 345.323 |  |  |  | 0.268 | 6202.253 | 318.197
0.264 | 6788.045 | 387.314 |  |  |  | 0.27 | 8525.104 | 261.425
0.266 | 5383.928 | 366.873 |  |  |  | 0.272 | 10316.307 | 242.557
0.268 | 5851.967 | 326.918 |  |  |  | 0.274 | 11107.472 | 249.087
0.27 | 8090.244 | 248.225 |  |  |  | 0.276 | 11170.765 | 248.607
0.272 | 10489.807 | 243.072 |  |  |  | 0.278 | 11265.705 | 268.845
0.274 | 11340.787 | 245.652 |  |  |  | 0.28 | 10506.187 | 302.258
0.276 | 11106.768 | 244.983 |  |  |  | 0.282 | 8649.588 | 339.765
0.278 | 11276.964 | 259.913 |  |  |  | 0.284 | 7737.112 | 369.163
0.28 | 10681.278 | 295.067 |  |  |  | 0.286 | 5964.904 | 342.366
0.282 | 9149.514 | 336.42 |  |  |  | 0.288 | 7657.995 | 301.855
0.284 | 7426.28 | 365.525 |  |  |  | 0.29 | 9366.91 | 270.452
0.286 | 5426.477 | 372.432 |  |  |  | 0.292 | 9493.497 | 300.435
0.288 | 7415.643 | 270.689 |  |  |  | 0.294 | 8702.332 | 324.956
0.29 | 9638.827 | 269.066 |  |  |  | 0.296 | 7911.168 | 333.87
0.292 | 9383.533 | 295.808 |  |  |  | 0.298 | 7626.349 | 307.079
0.294 | 8766.573 | 319.632 |  |  |  | 0.3 | 9113.738 | 275.302
0.296 | 8021.966 | 333.912 |  |  |  | 0.302 | 10063.135 | 236.814
0.298 | 7936.868 | 315.054 |  |  |  | 0.304 | 11756.227 | 230.28
0.3 | 8383.633 | 271.09 |  |  |  | 0.306 | 12436.628 | 224.748
0.302 | 10468.533 | 232.937 |  |  |  | 0.308 | 12594.861 | 223.017
0.304 | 11766.277 | 227.547 |  |  |  | 0.31 | 12151.809 | 243.396
0.306 | 12276.865 | 220.886 |  |  |  | 0.312 | 11866.989 | 270.335
0.308 | 12872.551 | 222.038 |  |  |  | 0.314 | 10242.465 | 335.313
0.31 | 12319.414 | 237.095 |  |  |  | 0.316 | 7199.12 | 402.937
0.312 | 11681.179 | 265.247 |  |  |  | 0.318 | 4493.338 | 416.37
0.314 | 11128.042 | 316.405 |  |  |  | 0.32 | 3733.82 | 413.715
0.315 | 9512.507 | 374.242 |  |  |  | 0.322 | 3480.648 | 418.018
0.316 | 7128.437 | 420.909 |  |  |  | 0.324 | 3069.242 | 425.469
0.317 | 5400.05 | 428.816 |  |  |  | 0.326 | 2721.13 | 430.634
0.318 | 4256.381 | 420.697 |  |  |  | 0.328 | 2626.19 | 433.14
0.32 | 3767.067 | 410.411 |  |  |  | 0.33 | 2562.897 | 434.022
0.322 | 3426.675 | 417.099 |  |  |  | 0.332 | 2404.664 | 432.342
0.324 | 3065.009 | 424.336 |  |  |  | 0.334 | 2404.664 | 433.605
0.326 | 2682.068 | 427.826 |  |  |  | 0.336 | 2341.371 | 436.82
0.328 | 2745.891 | 430.379 |  |  |  | 0.338 | 2341.371 | 426.861
0.33 | 2405.499 | 431.642 |  |  |  | 0.34 | 2816.07 | 408.476
0.332 | 2660.793 | 429.836 |  |  |  | 0.342 | 4113.579 | 389.409
0.334 | 2490.597 | 429.32 |  |  |  | 0.344 | 4366.752 | 379.945
0.336 | 2320.401 | 434.602 |  |  |  | 0.346 | 4778.157 | 383.806
0.338 | 2256.578 | 424.291 |  |  |  | 0.348 | 4651.571 | 395.009
0.34 | 3086.283 | 405.57 |  |  |  | 0.35 | 4240.166 | 401.495
0.342 | 3405.401 | 389.775 |  |  |  | 0.352 | 3892.053 | 403.938
0.344 | 4447.851 | 370.011 |  |  |  | 0.354 | 3797.114 | 410.173
0.346 | 4830.792 | 381.41 |  |  |  | 0.356 | 3543.941 | 417.886
0.348 | 4788.243 | 391.84 |  |  |  | 0.358 | 3164.182 | 422.349
0.35 | 3937.263 | 399.341 |  |  |  | 0.36 | 2816.07 | 420.655
0.352 | 3852.165 | 401.95 |  |  |  | 0.362 | 2974.303 | 420.361
0.354 | 3979.812 | 408.232 |  |  |  | 0.364 | 2879.363 | 427.879
0.356 | 3596.871 | 414.706 |  |  |  | 0.366 | 2626.19 | 432.286
0.358 | 3001.185 | 421.953 |  |  |  | 0.368 | 2436.311 | 432.117
0.36 | 2767.166 | 419.687 |  |  |  | 0.37 | 2436.311 | 436.153
0.362 | 3213.93 | 418.444 |  |  |  | 0.372 | 2246.432 | 440.024
0.364 | 2916.087 | 425.401 |  |  |  | 0.374 | 2056.552 | 439.686
0.366 | 2745.891 | 430.206 |  |  |  | 0.376 | 2151.492 | 444.094
0.368 | 2405.499 | 430.261 |  |  |  | 0.378 | 1898.319 | 447.727
0.37 | 2575.695 | 432.848 |  |  |  | 0.38 | 1835.026 | 444.155
0.372 | 2192.754 | 437.812 |  |  |  | 0.382 | 1929.966 | 443.25
0.374 | 1980.009 | 435.153 |  |  |  | 0.384 | 1866.673 | 448.155
0.376 | 2235.303 | 441.841 |  |  |  | 0.386 | 1645.147 | 457.516
0.378 | 1894.911 | 446.087 |  |  |  | 0.388 | 1328.681 | 455.209
0.38 | 1809.813 | 441.309 |  |  |  | 0.39 | 1550.207 | 430.018
0.382 | 2235.303 | 439.902 |  |  |  | 0.392 | 1486.914 | 458.926
0.384 | 1937.46 | 444.458 |  |  |  | 0.394 | 853.982 | 481.863
0.386 | 1682.166 | 455.756 |  |  |  | 0.396 | 1012.215 | 454.935
0.388 | 1214.127 | 458.687 |  |  |  | 0.398 | 1360.328 | 445.828
0.39 | 1682.166 | 435.52 |  |  |  | 0.4 | 1740.086 | 424.742
0.392 | 1724.715 | 464.253 |  |  |  | 0.402 | 1676.793 | 458.937
0.394 | 490.795 | 472.263 |  |  |  | 0.404 | 1360.328 | 460.485
0.396 | 1129.029 | 443.596 |  |  |  | 0.406 | 1328.681 | 446.29
0.398 | 1384.323 | 446.876 |  |  |  | 0.408 | 1107.155 | 475.891
0.4 | 1916.186 | 437.534 |  |  |  | 0.41 | 853.982 | 470.243
0.402 | 1469.421 | 458.547 |  |  |  | 0.412 | 822.336 | 469.675
0.404 | 1299.225 | 459.014 |  |  |  | 0.414 | 759.043 | 468.436
0.406 | 1341.774 | 456.605 |  |  |  | 0.416 | 695.75 | 461.285
0.408 | 831.187 | 470.208 |  |  |  | 0.418 | 505.87 | 486.095
0.41 | 746.089 | 465.246 |  |  |  | 0.42 | 505.87 | 464.608
0.412 | 873.736 | 467.888 |  |  |  | 0.422 | 600.81 | 480.167
0.414 | 746.089 | 466.126 |  |  |  | 0.424 | 474.224 | 482.269
0.416 | 660.991 | 469.439
0.418 | 363.148 | 477.535
0.42 | 405.697 | 466.041
0.422 | 660.991 | 474.678
0.424 | 278.05 | 482.476
0.426 | 150.403 | 479.264

## Test-2197
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2197
Scenario | 480V - 5kA Available Arc on battery side of breaker with Cabinet w/ Cover Plate A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 6", 74" high, next to breaker handle
Test Voltage (V) | 434.9
Arc Current (A) | 1915
Arc Voltage (V) | 306.2
Duration of Arc (s) | 0.01676
Arc Energy (kJ) | 9.145 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 0.07 |  | Test 23-2197 was taken inside of the battery cabinet at highest voltage and lowest current. Connections were made by replacing the existing circuit breaker with a spare circuit breaker. Additionally, a cover plate was installed near the terminals of the circuit breaker. This was to aid with mounting a new breaker, after damage was sustained from the previous tests. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. Only a quick spark and some minor smoke were observed. It was decided to proceed with the next test at the same voltage level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 0.1
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 2198.118 | 21.528 |  |  |  | 0.11 | 2141.401 | 24.041
0.111 | 4233.268 | 43.787 |  |  |  | 0.111 | 4056.725 | 39.074
0.112 | 4608.202 | 71.321 |  |  |  | 0.112 | 4664.591 | 52.768
0.113 | 4184.047 | 126.491 |  |  |  | 0.113 | 4041.454 | 150.301
0.114 | 3191.184 | 231.356 |  |  |  | 0.114 | 3085.266 | 234.618
0.115 | 2608.267 | 293.308 |  |  |  | 0.115 | 2669.931 | 290.982
0.116 | 1342.209 | 382.862 |  |  |  | 0.116 | 1551.87 | 378.186
0.117 | 1509.487 | 369.981 |  |  |  | 0.117 | 1352.352 | 364.818
0.118 | 2050.458 | 251.291 |  |  |  | 0.118 | 1996.407 | 293.334
0.119 | 2487.427 | 228.29 |  |  |  | 0.119 | 2534.549 | 235.291
0.12 | 2670.698 | 268.773 |  |  |  | 0.12 | 2673.093 | 245.273
0.121 | 2275.35 | 274.293 |  |  |  | 0.121 | 2390.98 | 266.37
0.122 | 1992.05 | 321.217 |  |  |  | 0.122 | 2030.224 | 319.24
0.123 | 1724.743 | 337.779 |  |  |  | 0.123 | 1602.643 | 336.104
0.124 | 1130.131 | 369.061 |  |  |  | 0.124 | 1267.95 | 316.791
0.125 | 2180.271 | 202.527 |  |  |  | 0.125 | 2358.631 | 245.236
0.126 | 2473.024 | 271.533 |  |  |  | 0.126 | 2464.543 | 256.811
0.127 | 2036.055 | 291.468 |  |  |  | 0.127 | 2286.254 | 294.859
0.128 | 1427.04 | 414.145 |  |  |  | 0.128 | 1603.527 | 405.735
0.129 | 1201.354 | 357.1 |  |  |  | 0.129 | 1275.515 | 376.203
0.13 | 695.546 | 468.122 |  |  |  | 0.13 | 744.502 | 463.266

## Test-2198
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2198
Scenario | 480V - 5kA Available Arc on battery side of breaker with Cabinet w/ Plexi Glass A: calorimeter at 18", 66" high, angled to breaker terminals : B: calorimeter at 8", 74" high, next to breaker handle
Test Voltage (V) | 434.9
Arc Current (A) | 1803
Arc Voltage (V) | 304.3
Duration of Arc (s) | 1.221
Arc Energy (kJ) | 639.2 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 2.6 |  | Test 23-2198 was taken inside of the battery cabinet at highest voltage and lowest current. Connections were made by applying a plexiglass near the front of the circuit breaker. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A significant blast, arcing, and black smoke were observed. Further investigation revealed that the metal plate that the circuit breaker mounted on had a hole through it. Review of high-speed video shows the arc was mainly contained within the battery cabinet, before growing outside of the battery cabinet towards just-below the calorimeters, and sustaining in that manner as a small fire until it is finally extinguished. Nonetheless, it was decided to proceed with the next test at the same current level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 4.11
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 2544.263 | 18.36 |  |  |  | 0.11 | 3523.224 | 39.096
0.115 | 3682.405 | 101.297 |  |  |  | 0.115 | 3808.558 | 91.449
0.12 | 3724.953 | 122.583 |  |  |  | 0.12 | 3681.743 | 124.759
0.125 | 3639.858 | 142.511 |  |  |  | 0.125 | 3428.113 | 168.749
0.13 | 1618.859 | 304.861 |  |  |  | 0.13 | 2952.555 | 291.975
0.135 | 916.827 | 397.798 |  |  |  | 0.135 | 925.2 | 403.624
0.14 | 484.382 | 448.875 |  |  |  | 0.14 | 456.372 | 448.04
0.145 | 558.999 | 439.917 |  |  |  | 0.145 | 521.042 | 444.456
0.15 | 789.185 | 407.922 |  |  |  | 0.15 | 821.304 | 414.667
0.155 | 1001.922 | 396.43 |  |  |  | 0.155 | 995.815 | 395.408
0.16 | 1087.017 | 381.392 |  |  |  | 0.16 | 1050.328 | 381.998
0.165 | 1129.564 | 373.928 |  |  |  | 0.165 | 1113.735 | 377.752
0.17 | 1044.47 | 382.735 |  |  |  | 0.17 | 1050.328 | 389.767
0.175 | 789.185 | 389.731 |  |  |  | 0.175 | 986.92 | 381.898
0.18 | 831.733 | 404.756 |  |  |  | 0.18 | 891.809 | 395.308
0.185 | 746.638 | 410.859 |  |  |  | 0.185 | 989.708 | 412.717
0.19 | 1129.564 | 369.165 |  |  |  | 0.19 | 1145.439 | 390.65
0.195 | 1087.017 | 391.762 |  |  |  | 0.195 | 923.512 | 395.583
0.2 | 746.638 | 415.873 |  |  |  | 0.2 | 788.206 | 412.415
0.21 | 1001.922 | 389.388 |  |  |  | 0.205 | 484.495 | 428.105
0.215 | 1044.47 | 365.525 |  |  |  | 0.21 | 1115.129 | 388.172
0.22 | 1512.49 | 338.944 |  |  |  | 0.215 | 1240.55 | 358.732
0.225 | 1767.774 | 325.469 |  |  |  | 0.22 | 1620.996 | 341.19
0.23 | 1852.869 | 307.418 |  |  |  | 0.225 | 1620.996 | 328.69
0.235 | 1469.943 | 334.057 |  |  |  | 0.23 | 1779.515 | 309.628
0.24 | 1384.848 | 338.916 |  |  |  | 0.235 | 1589.292 | 327.245
0.245 | 1767.774 | 322.297 |  |  |  | 0.24 | 1557.588 | 325.364
0.25 | 1597.585 | 320.905 |  |  |  | 0.245 | 1747.811 | 321.865
0.255 | 1555.038 | 331.518 |  |  |  | 0.25 | 1620.996 | 318.534
0.26 | 1767.774 | 320.424 |  |  |  | 0.255 | 1399.069 | 342.731
0.265 | 1469.943 | 340.344 |  |  |  | 0.26 | 1716.107 | 331.572
0.27 | 1172.112 | 364.223 |  |  |  | 0.265 | 1684.404 | 333.161
0.275 | 1469.943 | 355.741 |  |  |  | 0.27 | 2191.665 | 367.316
0.28 | 2320.89 | 264.067 |  |  |  | 0.275 | 2318.48 | 322.724
0.285 | 2023.059 | 292.774 |  |  |  | 0.28 | 2207.517 | 304.54
0.29 | 1682.68 | 308.334 |  |  |  | 0.285 | 1779.515 | 308.385
0.295 | 2576.174 | 244.669 |  |  |  | 0.29 | 1811.219 | 302.74
0.3 | 1257.206 | 341.455 |  |  |  | 0.295 | 2524.554 | 243.494
0.305 | 1384.848 | 333.962 |  |  |  | 0.3 | 1240.55 | 358.097
0.31 | 1512.49 | 343.759 |  |  |  | 0.305 | 1947.355 | 311.539
0.315 | 1512.49 | 334.559 |  |  |  | 0.31 | 1779.515 | 304.616
0.32 | 1597.585 | 323.616 |  |  |  | 0.315 | 1652.7 | 325.987
0.325 | 1469.943 | 343.076 |  |  |  | 0.32 | 2445.295 | 308.425
0.33 | 1640.132 | 317.862 |  |  |  | 0.325 | 1525.885 | 318.954
0.335 | 1725.227 | 323.581 |  |  |  | 0.33 | 1684.404 | 309.236
0.34 | 1172.112 | 349.56 |  |  |  | 0.335 | 1557.588 | 318.667
0.345 | 1725.227 | 293.349 |  |  |  | 0.34 | 2255.072 | 330.945
0.35 | 1427.396 | 362.373 |  |  |  | 0.345 | 1842.923 | 308.808
0.355 | 1469.943 | 314.547 |  |  |  | 0.35 | 2318.48 | 321.731
0.36 | 1597.585 | 326.926 |  |  |  | 0.355 | 2572.11 | 303.003
0.365 | 1937.964 | 294.344 |  |  |  | 0.36 | 1684.404 | 328.953
0.37 | 1640.132 | 335.719 |  |  |  | 0.365 | 1842.923 | 310.488
0.375 | 1895.417 | 311.691 |  |  |  | 0.37 | 1620.996 | 337.264
0.38 | 1640.132 | 323.823 |  |  |  | 0.375 | 1747.811 | 327.804
0.385 | 2065.606 | 295.832 |  |  |  | 0.38 | 1589.292 | 327.29
0.39 | 1469.943 | 326.014 |  |  |  | 0.385 | 1906.33 | 301.62
0.395 | 1512.49 | 318.981 |  |  |  | 0.39 | 1589.292 | 323.645
0.4 | 1512.49 | 336.929 |  |  |  | 0.395 | 1620.996 | 319.591
0.405 | 1384.848 | 350.884 |  |  |  | 0.4 | 1620.996 | 333.637
0.41 | 1640.132 | 326.915 |  |  |  | 0.405 | 1494.181 | 348.929
0.415 | 2023.059 | 290.516 |  |  |  | 0.41 | 1652.7 | 330.762
0.42 | 1682.68 | 319.561 |  |  |  | 0.415 | 1906.33 | 294.895
0.425 | 1384.848 | 346.959 |  |  |  | 0.42 | 1652.7 | 326.464
0.43 | 2023.059 | 282.113 |  |  |  | 0.425 | 1335.662 | 332.869
0.435 | 1810.322 | 304.308 |  |  |  | 0.43 | 1842.923 | 292.883
0.44 | 1640.132 | 324.169 |  |  |  | 0.435 | 1811.219 | 306.575
0.445 | 1640.132 | 333.89 |  |  |  | 0.44 | 1620.996 | 320.783
0.45 | 1725.227 | 296.974 |  |  |  | 0.445 | 1557.588 | 321.644
0.455 | 1725.227 | 311.979 |  |  |  | 0.45 | 1716.107 | 306.329
0.46 | 1597.585 | 323.284 |  |  |  | 0.455 | 1684.404 | 311.917
0.465 | 1597.585 | 330.575 |  |  |  | 0.46 | 1589.292 | 327.915
0.47 | 1725.227 | 318.13 |  |  |  | 0.465 | 1620.996 | 335.989
0.475 | 1640.132 | 306.755 |  |  |  | 0.47 | 1779.515 | 320.555
0.48 | 2065.606 | 295.65 |  |  |  | 0.475 | 1684.404 | 309.242
0.485 | 1682.68 | 331.476 |  |  |  | 0.48 | 1906.33 | 292.473
0.49 | 1257.206 | 372.503 |  |  |  | 0.485 | 1652.7 | 336.507
0.495 | 1640.132 | 306.081 |  |  |  | 0.49 | 1240.55 | 360.77
0.5 | 1597.585 | 319.331 |  |  |  | 0.495 | 1874.626 | 306.624
0.505 | 1640.132 | 330.171 |  |  |  | 0.5 | 1779.515 | 309.923
0.51 | 1257.206 | 353.704 |  |  |  | 0.505 | 1557.588 | 331.551
0.515 | 1448.669 | 339.857 |  |  |  | 0.51 | 1240.55 | 357.227
0.52 | 1427.396 | 350.741 |  |  |  | 0.515 | 1430.773 | 343.32
0.525 | 1469.943 | 318.919 |  |  |  | 0.52 | 1494.181 | 340.827
0.53 | 2576.174 | 288.062 |  |  |  | 0.525 | 1525.885 | 315.824
0.535 | 1767.774 | 312.61 |  |  |  | 0.53 | 2698.925 | 299.533
0.54 | 1555.038 | 327.099 |  |  |  | 0.535 | 1779.515 | 314.235
0.545 | 1725.227 | 317.676 |  |  |  | 0.54 | 1620.996 | 328.184
0.55 | 1682.68 | 296.137 |  |  |  | 0.545 | 1779.515 | 305.321
0.555 | 2193.248 | 267.121 |  |  |  | 0.55 | 1779.515 | 285.24
0.56 | 2320.89 | 248.757 |  |  |  | 0.555 | 2223.368 | 268.581
0.565 | 2491.079 | 243.638 |  |  |  | 0.56 | 2381.887 | 254.557
0.57 | 2363.437 | 253.443 |  |  |  | 0.565 | 2476.999 | 252.19
0.575 | 2320.89 | 254.327 |  |  |  | 0.57 | 2318.48 | 256.663
0.58 | 2320.89 | 253.694 |  |  |  | 0.575 | 2286.776 | 258.146
0.585 | 2235.795 | 254.792 |  |  |  | 0.58 | 2350.184 | 255.672
0.59 | 2278.343 | 258.089 |  |  |  | 0.585 | 2255.072 | 255.61
0.595 | 2363.437 | 254.517 |  |  |  | 0.59 | 2255.072 | 258.834
0.6 | 1980.511 | 285.611 |  |  |  | 0.595 | 2381.887 | 262.261
0.605 | 2065.606 | 281.495 |  |  |  | 0.6 | 2064.849 | 285.307
0.61 | 2278.343 | 264.65 |  |  |  | 0.605 | 2064.849 | 282.789
0.615 | 2065.606 | 280.284 |  |  |  | 0.61 | 2191.665 | 265.326
0.62 | 1852.869 | 293.849 |  |  |  | 0.615 | 2064.849 | 289.116
0.625 | 1852.869 | 308.64 |  |  |  | 0.62 | 1874.626 | 289.508
0.63 | 1597.585 | 323.445 |  |  |  | 0.625 | 1906.33 | 304.555
0.635 | 1767.774 | 314.314 |  |  |  | 0.63 | 1589.292 | 324.964
0.64 | 1767.774 | 325.22 |  |  |  | 0.635 | 1652.7 | 317.751
0.645 | 1767.774 | 309.373 |  |  |  | 0.64 | 1716.107 | 338.005
0.65 | 1895.417 | 293.675 |  |  |  | 0.645 | 1779.515 | 324.844
0.655 | 1980.511 | 300.496 |  |  |  | 0.65 | 1842.923 | 301.591
0.66 | 1725.227 | 313.874 |  |  |  | 0.655 | 1779.515 | 299.835
0.665 | 1852.869 | 311.256 |  |  |  | 0.66 | 1716.107 | 312.139
0.67 | 1852.869 | 313.497 |  |  |  | 0.665 | 1811.219 | 311.871
0.675 | 1895.417 | 296.42 |  |  |  | 0.67 | 1779.515 | 316.475
0.68 | 1767.774 | 315.455 |  |  |  | 0.675 | 1779.515 | 320.377
0.685 | 2065.606 | 280.431 |  |  |  | 0.68 | 1684.404 | 312.21
0.69 | 2150.701 | 268.666 |  |  |  | 0.685 | 2128.257 | 285.396
0.695 | 2320.89 | 254.246 |  |  |  | 0.69 | 2159.961 | 268.528
0.7 | 2491.079 | 244.129 |  |  |  | 0.695 | 2318.48 | 256.511
0.705 | 2405.985 | 253.173 |  |  |  | 0.7 | 2445.295 | 245.209
0.71 | 2320.89 | 259.069 |  |  |  | 0.705 | 2350.184 | 257.498
0.715 | 2108.153 | 273.811 |  |  |  | 0.71 | 2286.776 | 263.166
0.72 | 1980.511 | 294.052 |  |  |  | 0.715 | 2128.257 | 276.502
0.725 | 1895.417 | 291.685 |  |  |  | 0.72 | 1938.034 | 295.187
0.73 | 2023.059 | 283.484 |  |  |  | 0.725 | 1906.33 | 294.907
0.735 | 2235.795 | 257.299 |  |  |  | 0.73 | 2001.442 | 283.032
0.74 | 2533.627 | 237.442 |  |  |  | 0.735 | 2255.072 | 266.946
0.745 | 2235.795 | 249.395 |  |  |  | 0.74 | 2476.999 | 245.531
0.75 | 2618.721 | 232.061 |  |  |  | 0.745 | 2350.184 | 244.34
0.755 | 2363.437 | 260.323 |  |  |  | 0.75 | 2508.703 | 239.479
0.76 | 1980.511 | 284.87 |  |  |  | 0.755 | 2223.368 | 261.997
0.765 | 1937.964 | 293.763 |  |  |  | 0.76 | 2033.146 | 272.384
0.77 | 1895.417 | 304.271 |  |  |  | 0.765 | 1938.034 | 293.477
0.775 | 1852.869 | 295.887 |  |  |  | 0.77 | 1842.923 | 305.417
0.78 | 1937.964 | 293.932 |  |  |  | 0.775 | 1811.219 | 297.237
0.785 | 2023.059 | 298.222 |  |  |  | 0.78 | 1906.33 | 295.615
0.79 | 1937.964 | 301.538 |  |  |  | 0.785 | 2001.442 | 299.795
0.795 | 1937.964 | 295.819 |  |  |  | 0.79 | 1906.33 | 301.74
0.8 | 1937.964 | 294.563 |  |  |  | 0.795 | 1811.219 | 296.545
0.805 | 2023.059 | 292.785 |  |  |  | 0.8 | 1811.219 | 295.714
0.81 | 1937.964 | 293.682 |  |  |  | 0.805 | 1874.626 | 294.803
0.815 | 1895.417 | 287.746 |  |  |  | 0.81 | 1906.33 | 292.869
0.82 | 1980.511 | 283.914 |  |  |  | 0.815 | 2001.442 | 285.809
0.825 | 2108.153 | 282.364 |  |  |  | 0.82 | 2096.553 | 283.046
0.83 | 1937.964 | 296.904 |  |  |  | 0.825 | 2033.146 | 286.06
0.835 | 1980.511 | 293.457 |  |  |  | 0.83 | 1969.738 | 293.582
0.84 | 1810.322 | 304.65 |  |  |  | 0.835 | 1938.034 | 294.676
0.845 | 1895.417 | 311.389 |  |  |  | 0.84 | 1779.515 | 302.572
0.85 | 1427.396 | 336.647 |  |  |  | 0.845 | 1811.219 | 314.186
0.855 | 1384.848 | 323.807 |  |  |  | 0.85 | 1494.181 | 344.167
0.86 | 1895.417 | 297.584 |  |  |  | 0.855 | 1430.773 | 342.97
0.865 | 2150.701 | 264.851 |  |  |  | 0.86 | 1874.626 | 300.68
0.87 | 2448.532 | 245.126 |  |  |  | 0.865 | 2128.257 | 273.986
0.875 | 2448.532 | 245.083 |  |  |  | 0.87 | 2413.591 | 244.458
0.88 | 2405.985 | 252.078 |  |  |  | 0.875 | 2350.184 | 244.247
0.885 | 2320.89 | 259.866 |  |  |  | 0.88 | 2318.48 | 251.699
0.89 | 2150.701 | 272.107 |  |  |  | 0.885 | 2318.48 | 262.977
0.895 | 1980.511 | 291.17 |  |  |  | 0.89 | 2128.257 | 276.036
0.9 | 2235.795 | 309.685 |  |  |  | 0.895 | 2001.442 | 290.817
0.905 | 1767.774 | 306.6 |  |  |  | 0.9 | 1747.811 | 304.961
0.91 | 1597.585 | 307.312 |  |  |  | 0.905 | 1779.515 | 305.432
0.915 | 2023.059 | 295.432 |  |  |  | 0.91 | 1684.404 | 304.391
0.92 | 2023.059 | 291.189 |  |  |  | 0.915 | 1938.034 | 293.126
0.925 | 2193.248 | 272.363 |  |  |  | 0.92 | 2001.442 | 289.142
0.93 | 2448.532 | 251.242 |  |  |  | 0.925 | 2128.257 | 275.197
0.935 | 2448.532 | 249.672 |  |  |  | 0.93 | 2318.48 | 259.615
0.94 | 2320.89 | 247.329 |  |  |  | 0.935 | 2413.591 | 255.771
0.945 | 2363.437 | 254.635 |  |  |  | 0.94 | 2350.184 | 251.982
0.95 | 2193.248 | 274.976 |  |  |  | 0.945 | 2350.184 | 255.389
0.955 | 1895.417 | 311.87 |  |  |  | 0.95 | 2064.849 | 278.856
0.96 | 1640.132 | 304.45 |  |  |  | 0.955 | 1906.33 | 318.688
0.965 | 2405.985 | 250.109 |  |  |  | 0.96 | 1747.811 | 302.823
0.97 | 2491.079 | 246.554 |  |  |  | 0.965 | 2350.184 | 264.403
0.975 | 2278.343 | 250.323 |  |  |  | 0.97 | 2445.295 | 247.814
0.98 | 1937.964 | 303.455 |  |  |  | 0.975 | 2381.887 | 252.635
0.985 | 1767.774 | 300.907 |  |  |  | 0.98 | 2096.553 | 289.705
0.99 | 1640.132 | 316.294 |  |  |  | 0.985 | 1906.33 | 307.277
0.995 | 1725.227 | 317.026 |  |  |  | 0.99 | 1652.7 | 307.692
1 | 1959.238 | 293.06 |  |  |  | 0.995 | 1716.107 | 313.569
1.005 | 1810.322 | 304.031 |  |  |  | 1 | 1842.923 | 289.264
1.01 | 1725.227 | 313.834 |  |  |  | 1.005 | 1811.219 | 304.247
1.015 | 1810.322 | 309.869 |  |  |  | 1.01 | 1684.404 | 317.588
1.02 | 1852.869 | 300.58 |  |  |  | 1.015 | 1811.219 | 312.866
1.025 | 2788.911 | 218.837 |  |  |  | 1.02 | 1779.515 | 303.351
1.03 | 3384.574 | 152.367 |  |  |  | 1.025 | 2698.925 | 234.643
1.035 | 3214.384 | 166.973 |  |  |  | 1.03 | 3364.705 | 157.562
1.04 | 2320.89 | 257.26 |  |  |  | 1.035 | 3174.482 | 184.14
1.045 | 1682.68 | 308.395 |  |  |  | 1.04 | 3333.001 | 249.338
1.05 | 1555.038 | 328.804 |  |  |  | 1.045 | 2445.295 | 338.525
1.055 | 1725.227 | 346.304 |  |  |  | 1.05 | 1557.588 | 353.566
1.06 | 1725.227 | 310.841 |  |  |  | 1.055 | 2128.257 | 372.412
1.065 | 1852.869 | 294.68 |  |  |  | 1.06 | 1716.107 | 321.309
1.07 | 1767.774 | 309.725 |  |  |  | 1.065 | 1652.7 | 303.284
1.075 | 1980.511 | 294.253 |  |  |  | 1.07 | 1811.219 | 309.834
1.08 | 1980.511 | 295.135 |  |  |  | 1.075 | 1938.034 | 299.868
1.085 | 1852.869 | 292.586 |  |  |  | 1.08 | 1938.034 | 302.171
1.09 | 1852.869 | 319.802 |  |  |  | 1.085 | 1906.33 | 302.653
1.095 | 1725.227 | 315.151 |  |  |  | 1.09 | 1652.7 | 318.194
1.1 | 1767.774 | 311.466 |  |  |  | 1.095 | 1589.292 | 319.451
1.105 | 1810.322 | 301.999 |  |  |  | 1.1 | 1747.811 | 314.456
1.11 | 1597.585 | 329.633 |  |  |  | 1.105 | 1874.626 | 301.422
1.115 | 1640.132 | 312.686 |  |  |  | 1.11 | 1747.811 | 333.361
1.12 | 1427.396 | 355.823 |  |  |  | 1.115 | 1620.996 | 325.933
1.125 | 1469.943 | 347.65 |  |  |  | 1.12 | 1335.662 | 343.693
1.13 | 1384.848 | 333.801 |  |  |  | 1.125 | 1430.773 | 350.857
1.135 | 1682.68 | 320.518 |  |  |  | 1.13 | 1399.069 | 328.306
1.14 | 1895.417 | 290.736 |  |  |  | 1.135 | 1747.811 | 309.602
1.145 | 1810.322 | 311.016 |  |  |  | 1.14 | 1811.219 | 295.317
1.15 | 1810.322 | 298.654 |  |  |  | 1.145 | 1747.811 | 308.045
1.155 | 2150.701 | 273.804 |  |  |  | 1.15 | 1811.219 | 299.995
1.16 | 2235.795 | 263.004 |  |  |  | 1.155 | 2128.257 | 275.823
1.165 | 2363.437 | 250.113 |  |  |  | 1.16 | 2286.776 | 261.971
1.17 | 2576.174 | 236.077 |  |  |  | 1.165 | 2255.072 | 248.248
1.175 | 2491.079 | 245.254 |  |  |  | 1.17 | 2540.406 | 244.037
1.18 | 2448.532 | 246.33 |  |  |  | 1.175 | 2413.591 | 243.822
1.185 | 2278.343 | 258.764 |  |  |  | 1.18 | 2413.591 | 247.241
1.19 | 2065.606 | 279.66 |  |  |  | 1.185 | 2286.776 | 258.689
1.195 | 2065.606 | 285.29 |  |  |  | 1.19 | 2033.146 | 274.857
1.2 | 2065.606 | 274.119 |  |  |  | 1.195 | 2033.146 | 283.006
1.205 | 1895.417 | 293.227 |  |  |  | 1.2 | 2064.849 | 281.185
1.21 | 2065.606 | 294.083 |  |  |  | 1.205 | 1842.923 | 293.459
1.215 | 1895.417 | 299.974 |  |  |  | 1.21 | 1969.738 | 295.274
1.22 | 1937.964 | 289.084 |  |  |  | 1.215 | 1811.219 | 299.209
1.225 | 2150.701 | 271.461 |  |  |  | 1.22 | 2128.257 | 282.136
1.23 | 2278.343 | 259.857 |  |  |  | 1.225 | 2286.776 | 270.11
1.235 | 2278.343 | 256.784 |  |  |  | 1.23 | 2255.072 | 264.108
1.24 | 2108.153 | 269.071 |  |  |  | 1.235 | 2286.776 | 260.847
1.245 | 1895.417 | 295.054 |  |  |  | 1.24 | 2223.368 | 267.298
1.25 | 2065.606 | 273.403 |  |  |  | 1.245 | 1874.626 | 300.643
1.255 | 1767.774 | 298.618 |  |  |  | 1.25 | 2096.553 | 277.026
1.26 | 1980.511 | 299.978 |  |  |  | 1.255 | 2001.442 | 293.104
1.265 | 2959.1 | 218.828 |  |  |  | 1.26 | 1969.738 | 276.792
1.27 | 2193.248 | 268.675 |  |  |  | 1.265 | 2746.481 | 211.659
1.275 | 1852.869 | 291.008 |  |  |  | 1.27 | 2381.887 | 256.172
1.28 | 1980.511 | 300.067 |  |  |  | 1.275 | 1842.923 | 289.602
1.285 | 1980.511 | 298.949 |  |  |  | 1.28 | 1906.33 | 301.46
1.29 | 1555.038 | 323.795 |  |  |  | 1.285 | 1779.515 | 306.403
1.295 | 1767.774 | 316.141 |  |  |  | 1.29 | 1557.588 | 320.747
1.3 | 1640.132 | 324.062 |  |  |  | 1.295 | 1779.515 | 314.658
1.305 | 1725.227 | 314.306 |  |  |  | 1.3 | 1620.996 | 329.441
1.31 | 1512.49 | 328.094 |  |  |  | 1.305 | 1747.811 | 318.968
1.315 | 1682.68 | 325.028 |  |  |  | 1.31 | 1525.885 | 319.179
1.32 | 1469.943 | 330.615 |  |  |  | 1.315 | 1652.7 | 326.844
1.325 | 1512.49 | 337.819 |  |  |  | 1.32 | 1589.292 | 335.984
1.33 | 1299.754 | 366.952 |  |  |  | 1.325 | 1557.588 | 343.663
1.335 | 979.055 | 415.778 |  |  |  | 1.33 | 1145.439 | 366.77
[6 empty] | 1.335 | 1874.626 | 416.554

## Test-2199
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2199
Scenario | 480V - 5kA Available Arc on battery side of breaker with Cabinet w/ Mannequin A: calorimeter at 20", 66" high, over Mannequin Shoulder : B: calorimeter at 12", 74" high, to breaker terminals
Test Voltage (V) | 434.9
Arc Current (A) | 1621
Arc Voltage (V) | 318.4
Duration of Arc (s) | 4.533
Arc Energy (kJ) | 2259 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 1.3 |  | Test 23-2199 was taken inside of the battery cabinet at highest voltage and lowest current. Connections were made by installing a plate to cover the hole where the circuit breaker mounts. Additionally, a mannequin was installed with the arm near the terminals of ther circuit breaker. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. A significant blast, and black smoke were observed, followed by continuous arcing and eventually a fire near the terminals of the circuit breaker. As a result, the circuit breaker could no longer be used. Nonetheless it was decided to proceed with the next test at a higher current level.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 5000 | 0 | Incident Energy at 6" distance (cal/cm²) | 6.36
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.11 | 2643.254 | 78.722 |  |  |  | 0.1 | 3181.074 | 65.818
0.12 | 3661.377 | 120.534 |  |  |  | 0.12 | 3181.074 | 121.39
0.14 | 3233.504 | 165.881 |  |  |  | 0.14 | 3244.616 | 160.225
0.16 | 3447.44 | 186.753 |  |  |  | 0.16 | 2831.589 | 190.627
0.18 | 2805.632 | 206.533 |  |  |  | 0.18 | 2768.047 | 206.489
0.2 | 3105.142 | 231.092 |  |  |  | 0.2 | 3244.616 | 226.762
0.22 | 2206.61 | 255.11 |  |  |  | 0.22 | 2196.163 | 251.864
0.24 | 2933.993 | 245.318 |  |  |  | 0.24 | 2323.248 | 251.495
0.26 | 2121.036 | 270.838 |  |  |  | 0.26 | 2132.621 | 249.408
0.28 | 2484.727 | 247.528 |  |  |  | 0.28 | 2339.134 | 243.199
0.3 | 2591.696 | 255.359 |  |  |  | 0.3 | 2482.105 | 241.79
0.32 | 2035.461 | 279.873 |  |  |  | 0.32 | 2005.535 | 264.649
0.34 | 1949.886 | 281.31 |  |  |  | 0.34 | 1910.221 | 277.752
0.36 | 2356.365 | 256.497 |  |  |  | 0.36 | 2275.592 | 258.647
0.38 | 2121.036 | 262.592 |  |  |  | 0.38 | 2132.621 | 257.931
0.4 | 1949.886 | 274.144 |  |  |  | 0.4 | 1973.764 | 264.99
0.42 | 1949.886 | 280.733 |  |  |  | 0.42 | 1846.679 | 265.159
0.44 | 2334.972 | 253.163 |  |  |  | 0.44 | 2196.163 | 256.872
0.46 | 2377.759 | 253.504 |  |  |  | 0.46 | 2196.163 | 261.71
0.48 | 2762.844 | 266.396 |  |  |  | 0.48 | 2863.361 | 265.869
0.5 | 2184.175 | 282.005 |  |  |  | 0.5 | 2037.307 | 283.367
0.52 | 1949.886 | 274.45 |  |  |  | 0.52 | 2212.049 | 265.207
0.54 | 2677.27 | 239.184 |  |  |  | 0.54 | 2307.363 | 243.331
0.56 | 2057.896 | 269.33 |  |  |  | 0.56 | 2100.849 | 267.528
0.58 | 2591.695 | 274.637 |  |  |  | 0.58 | 2037.307 | 273.544
0.6 | 1949.886 | 287.211 |  |  |  | 0.6 | 1910.221 | 272.81
0.62 | 2078.248 | 275.711 |  |  |  | 0.62 | 2100.849 | 263.382
0.64 | 2377.759 | 251.759 |  |  |  | 0.64 | 2291.477 | 250.147
0.66 | 2463.334 | 233.84 |  |  |  | 0.66 | 2418.562 | 247.603
0.68 | 2591.695 | 269.222 |  |  |  | 0.68 | 2799.818 | 265.473
0.7 | 2035.461 | 278.071 |  |  |  | 0.7 | 2736.275 | 274.941
0.72 | 1864.312 | 285.02 |  |  |  | 0.72 | 2005.535 | 269.05
0.74 | 2548.908 | 256.057 |  |  |  | 0.74 | 2339.134 | 258.467
0.76 | 2121.036 | 277.09 |  |  |  | 0.76 | 2100.849 | 267.281
0.78 | 2506.121 | 275.359 |  |  |  | 0.78 | 2736.275 | 269.888
0.8 | 2334.972 | 267.632 |  |  |  | 0.8 | 2132.621 | 271.32
0.82 | 1821.525 | 292.022 |  |  |  | 0.82 | 1814.907 | 282.695
0.84 | 1821.525 | 295.789 |  |  |  | 0.84 | 1814.907 | 274.951
0.86 | 2292.184 | 271.144 |  |  |  | 0.86 | 2196.163 | 260.839
0.88 | 2634.483 | 235.12 |  |  |  | 0.88 | 2434.448 | 246.225
0.9 | 1949.886 | 293.607 |  |  |  | 0.9 | 2148.507 | 260.907
0.92 | 2249.398 | 275.356 |  |  |  | 0.92 | 2116.735 | 274.697
0.94 | 2035.461 | 293.699 |  |  |  | 0.94 | 2021.421 | 277.747
0.96 | 1778.737 | 295.958 |  |  |  | 0.96 | 2672.733 | 289.499
0.98 | 1949.886 | 296.899 |  |  |  | 0.98 | 1878.45 | 295.181
1 | 1778.737 | 297.625 |  |  |  | 1 | 1783.136 | 292.503
1.02 | 1778.737 | 308.828 |  |  |  | 1.02 | 1783.136 | 306.012
1.04 | 1735.95 | 312.874 |  |  |  | 1.04 | 1687.822 | 313.809
1.06 | 1778.737 | 307.666 |  |  |  | 1.06 | 1687.822 | 293.169
1.08 | 2078.248 | 289.929 |  |  |  | 1.08 | 1941.993 | 284.883
1.1 | 1864.312 | 290.12 |  |  |  | 1.1 | 1941.993 | 280.925
1.12 | 2163.823 | 285.083 |  |  |  | 1.12 | 1973.764 | 279.511
1.14 | 1992.674 | 292.429 |  |  |  | 1.14 | 1910.221 | 295.329
1.16 | 1735.95 | 305.979 |  |  |  | 1.16 | 1687.822 | 299.632
1.18 | 1907.099 | 301.719 |  |  |  | 1.18 | 1814.907 | 288.948
1.2 | 1821.525 | 302.367 |  |  |  | 1.2 | 1814.907 | 302.195
1.22 | 1778.737 | 308.469 |  |  |  | 1.22 | 1719.594 | 305.596
1.24 | 1650.376 | 314.58 |  |  |  | 1.24 | 1624.28 | 307.365
1.26 | 1735.95 | 313.914 |  |  |  | 1.26 | 1687.822 | 311.882
1.28 | 1650.376 | 315.672 |  |  |  | 1.28 | 1624.28 | 309.517
1.3 | 1650.376 | 321.471 |  |  |  | 1.3 | 1624.28 | 309.267
1.32 | 1564.801 | 320.331 |  |  |  | 1.32 | 1560.737 | 310.364
1.34 | 1564.801 | 321.674 |  |  |  | 1.34 | 1528.966 | 312.773
1.36 | 1564.801 | 324.903 |  |  |  | 1.36 | 1528.966 | 320.254
1.38 | 1650.376 | 332.893 |  |  |  | 1.38 | 1592.508 | 324.287
1.4 | 1735.95 | 326.411 |  |  |  | 1.4 | 1592.508 | 324.812
1.42 | 1522.014 | 329.905 |  |  |  | 1.42 | 1465.423 | 326.174
1.44 | 1564.801 | 326.854 |  |  |  | 1.44 | 1592.508 | 325.337
1.46 | 1479.227 | 327.304 |  |  |  | 1.46 | 1592.508 | 321.465
1.48 | 1564.801 | 335.836 |  |  |  | 1.48 | 1497.194 | 334.847
1.5 | 1479.227 | 333.198 |  |  |  | 1.5 | 1433.652 | 331.505
1.52 | 1650.376 | 329.048 |  |  |  | 1.52 | 1560.737 | 317.71
1.54 | 1564.801 | 329.052 |  |  |  | 1.54 | 1528.966 | 320.81
1.56 | 1479.227 | 334.677 |  |  |  | 1.56 | 1433.652 | 329.166
1.58 | 1479.227 | 333.234 |  |  |  | 1.58 | 1433.652 | 326.745
1.6 | 1564.801 | 329.84 |  |  |  | 1.6 | 1528.966 | 328.683
1.62 | 1564.801 | 329.968 |  |  |  | 1.62 | 1528.966 | 325.201
1.64 | 1479.227 | 330.696 |  |  |  | 1.64 | 1465.423 | 326.271
1.66 | 1564.801 | 328.493 |  |  |  | 1.66 | 1497.194 | 331.451
1.68 | 1693.163 | 325.917 |  |  |  | 1.68 | 1624.28 | 317.729
1.7 | 1607.588 | 325.059 |  |  |  | 1.7 | 1560.737 | 317.828
1.72 | 1607.588 | 322.549 |  |  |  | 1.72 | 1592.508 | 318.372
1.74 | 1607.589 | 328.443 |  |  |  | 1.74 | 2545.648 | 315.468
1.76 | 1522.014 | 333.528 |  |  |  | 1.76 | 1465.423 | 320.045
1.78 | 1564.801 | 327.028 |  |  |  | 1.78 | 1592.508 | 314.244
1.8 | 1564.801 | 325.086 |  |  |  | 1.8 | 1592.508 | 310.489
1.82 | 1842.918 | 309.581 |  |  |  | 1.82 | 1865.718 | 304.745
1.84 | 1522.014 | 310.205 |  |  |  | 1.84 | 1865.718 | 301.184
1.86 | 1949.887 | 306.653 |  |  |  | 1.86 | 1895.109 | 300.091
1.88 | 1778.737 | 305.034 |  |  |  | 1.88 | 1751.365 | 301.692
1.9 | 1607.588 | 319.69 |  |  |  | 1.9 | 1560.737 | 324.416
1.92 | 1607.588 | 323.194 |  |  |  | 1.92 | 1560.737 | 311.052
1.94 | 1650.376 | 324.772 |  |  |  | 1.94 | 1624.28 | 326.985
1.96 | 1522.014 | 330.158 |  |  |  | 1.96 | 1497.194 | 324.212
1.98 | 1522.014 | 332.677 |  |  |  | 1.98 | 1465.423 | 319.768
2 | 1564.801 | 331.895 |  |  |  | 2 | 1560.737 | 318.995
2.02 | 1522.014 | 327.776 |  |  |  | 2.02 | 1497.194 | 317.427
2.04 | 1522.014 | 328.885 |  |  |  | 2.04 | 1497.194 | 321.131
2.06 | 1564.801 | 330.423 |  |  |  | 2.06 | 1528.966 | 330.963
2.08 | 1522.014 | 329.625 |  |  |  | 2.08 | 1560.737 | 319.985
2.1 | 1564.801 | 333.653 |  |  |  | 2.1 | 1528.966 | 328.391
2.12 | 1522.014 | 334.598 |  |  |  | 2.12 | 1497.194 | 338.528
2.14 | 1479.227 | 330.502 |  |  |  | 2.14 | 1465.423 | 321.4
2.16 | 1607.588 | 326.559 |  |  |  | 2.16 | 1560.737 | 323.232
2.18 | 1564.801 | 323.028 |  |  |  | 2.18 | 1560.737 | 328.248
2.2 | 1735.95 | 324.815 |  |  |  | 2.2 | 1624.28 | 308.982
2.22 | 1564.801 | 327.82 |  |  |  | 2.22 | 1528.966 | 323.85
2.24 | 1479.227 | 332.156 |  |  |  | 2.24 | 1497.194 | 321.405
2.26 | 1564.801 | 328.129 |  |  |  | 2.26 | 1528.966 | 318.44
2.28 | 1607.588 | 327.522 |  |  |  | 2.28 | 1624.28 | 329.388
2.3 | 1350.865 | 340.469 |  |  |  | 2.3 | 1338.338 | 340.878
2.32 | 1479.227 | 339.307 |  |  |  | 2.32 | 1401.88 | 329.827
2.34 | 1479.227 | 334.973 |  |  |  | 2.34 | 1433.652 | 336.295
2.36 | 1479.227 | 337.008 |  |  |  | 2.36 | 1465.423 | 332.254
2.38 | 1479.227 | 338.548 |  |  |  | 2.38 | 1465.423 | 329.274
2.4 | 1564.801 | 323.963 |  |  |  | 2.4 | 1802.175 | 319.723
2.42 | 2249.397 | 269.359 |  |  |  | 2.42 | 1819.251 | 311.389
2.44 | 1436.439 | 338.509 |  |  |  | 2.44 | 1401.88 | 324.421
2.46 | 1350.865 | 336.002 |  |  |  | 2.46 | 1433.652 | 324.098
2.48 | 1436.439 | 340.259 |  |  |  | 2.48 | 1433.652 | 325.691
2.5 | 1628.982 | 316.869 |  |  |  | 2.5 | 1624.28 | 318.548
2.52 | 1393.652 | 344.507 |  |  |  | 2.52 | 1640.939 | 315.6
2.54 | 2163.823 | 305.194 |  |  |  | 2.54 | 1592.508 | 305.715
2.56 | 1735.95 | 307.285 |  |  |  | 2.56 | 2227.934 | 275.674
2.58 | 2142.429 | 264.513 |  |  |  | 2.58 | 2386.791 | 263.687
2.6 | 2441.94 | 246.006 |  |  |  | 2.6 | 2307.363 | 265.756
2.62 | 2334.972 | 309.78 |  |  |  | 2.62 | 1878.45 | 298.034
2.64 | 1650.376 | 317.686 |  |  |  | 2.64 | 1592.508 | 314.433
2.66 | 1607.588 | 334.368 |  |  |  | 2.66 | 1528.966 | 322.537
2.68 | 1479.227 | 328.711 |  |  |  | 2.68 | 1370.109 | 329.463
2.7 | 1393.652 | 350.292 |  |  |  | 2.7 | 1370.109 | 334.519
2.72 | 1564.801 | 334.467 |  |  |  | 2.72 | 1465.423 | 326.567
2.74 | 1564.801 | 322.289 |  |  |  | 2.74 | 1560.737 | 321.161
2.76 | 1522.014 | 318.286 |  |  |  | 2.76 | 1560.737 | 315.522
2.78 | 1693.163 | 316.987 |  |  |  | 2.78 | 1624.28 | 311.306
2.8 | 1735.95 | 310.549 |  |  |  | 2.8 | 1687.822 | 313.416
2.82 | 1907.099 | 295.856 |  |  |  | 2.82 | 1878.45 | 291.292
2.84 | 2035.461 | 286.043 |  |  |  | 2.84 | 1973.764 | 284.853
2.86 | 1864.312 | 291.45 |  |  |  | 2.86 | 1814.907 | 286.323
2.88 | 2206.61 | 271.627 |  |  |  | 2.88 | 2084.964 | 271.304
2.9 | 1821.525 | 301.968 |  |  |  | 2.9 | 1751.365 | 282.523
2.92 | 1778.737 | 302.445 |  |  |  | 2.92 | 1783.136 | 291.441
2.94 | 1778.737 | 306.333 |  |  |  | 2.94 | 1656.051 | 311.212
2.96 | 1522.014 | 336.831 |  |  |  | 2.96 | 1624.28 | 326.153
2.98 | 1992.674 | 334.566 |  |  |  | 2.98 | 1528.966 | 333.446
3 | 1222.503 | 356.74 |  |  |  | 3 | 1211.253 | 339.753
3.02 | 1650.376 | 326.089 |  |  |  | 3.02 | 1433.652 | 329.668
3.04 | 1735.95 | 314.676 |  |  |  | 3.04 | 1687.822 | 312.307
3.06 | 1564.801 | 327.044 |  |  |  | 3.06 | 1560.737 | 323.192
3.08 | 1607.589 | 334.088 |  |  |  | 3.08 | 2227.934 | 333.487
3.1 | 1350.865 | 344.102 |  |  |  | 3.1 | 1370.109 | 331.472
3.12 | 1628.982 | 323.617 |  |  |  | 3.12 | 1941.576 | 297.755
3.14 | 2056.854 | 300.851 |  |  |  | 3.14 | 1973.764 | 295.696
3.16 | 1393.652 | 342.777 |  |  |  | 3.16 | 1401.88 | 325.899
3.18 | 1350.865 | 346.768 |  |  |  | 3.18 | 1338.338 | 336.85
3.2 | 1393.652 | 346.197 |  |  |  | 3.2 | 1370.109 | 335.166
3.22 | 2035.461 | 293.804 |  |  |  | 3.22 | 2164.392 | 277.818
3.24 | 2356.365 | 262.771 |  |  |  | 3.24 | 2402.677 | 260.68
3.26 | 2506.121 | 285.327 |  |  |  | 3.26 | 1973.764 | 288.572
3.28 | 2035.461 | 281.292 |  |  |  | 3.28 | 2005.535 | 287.726
3.3 | 2163.823 | 277.008 |  |  |  | 3.3 | 2005.535 | 284.274
3.32 | 1992.674 | 300.861 |  |  |  | 3.32 | 2022.194 | 294.401
3.34 | 1864.312 | 299.266 |  |  |  | 3.34 | 2005.119 | 294.007
3.36 | 1821.525 | 294.401 |  |  |  | 3.36 | 1878.45 | 288.481
3.38 | 2121.036 | 293.49 |  |  |  | 3.38 | 2021.421 | 280.981
3.4 | 1693.163 | 310.14 |  |  |  | 3.4 | 1687.822 | 291.287
3.42 | 1907.099 | 296.232 |  |  |  | 3.42 | 1973.764 | 300.38
3.44 | 2035.461 | 307.809 |  |  |  | 3.44 | 2672.733 | 312.014
3.46 | 2249.397 | 317.541 |  |  |  | 3.46 | 2482.105 | 309.273
3.48 | 1479.227 | 341.38 |  |  |  | 3.48 | 1338.338 | 340.962
3.5 | 1907.1 | 312.583 |  |  |  | 3.5 | 2672.733 | 307.671
3.52 | 1436.439 | 312.326 |  |  |  | 3.52 | 2672.733 | 307.162
3.54 | 1992.674 | 338.638 |  |  |  | 3.54 | 2100.849 | 347.701
3.56 | 1522.014 | 349.396 |  |  |  | 3.56 | 1306.567 | 345.753
3.58 | 1436.439 | 342.125 |  |  |  | 3.58 | 1401.88 | 353.936
3.6 | 1479.227 | 369.998 |  |  |  | 3.6 | 2037.307 | 373.355
3.62 | 1222.503 | 345.372 |  |  |  | 3.62 | 1306.567 | 349.058
3.64 | 1179.716 | 352.292 |  |  |  | 3.64 | 1179.481 | 348.727
3.66 | 1821.525 | 351.862 |  |  |  | 3.66 | 1243.024 | 356.295
3.68 | 1522.014 | 342.767 |  |  |  | 3.68 | 1433.652 | 335.684
3.7 | 1479.227 | 339.787 |  |  |  | 3.7 | 1465.423 | 336.938
3.72 | 1436.439 | 340.819 |  |  |  | 3.72 | 1370.109 | 339.965
3.74 | 1436.439 | 340.844 |  |  |  | 3.74 | 1401.88 | 338.475
3.76 | 1393.652 | 341.095 |  |  |  | 3.76 | 1370.109 | 342.835
3.78 | 1479.227 | 345.244 |  |  |  | 3.78 | 1370.109 | 346.859
3.8 | 1479.227 | 347.381 |  |  |  | 3.8 | 1243.024 | 342.567
3.82 | 1393.652 | 344.472 |  |  |  | 3.82 | 1243.024 | 335.448
3.84 | 1479.227 | 339.023 |  |  |  | 3.84 | 1401.88 | 334.602
3.86 | 1479.227 | 338.822 |  |  |  | 3.86 | 1401.88 | 338.964
3.88 | 1436.439 | 341.047 |  |  |  | 3.88 | 1370.109 | 343.233
3.9 | 1436.439 | 340.749 |  |  |  | 3.9 | 1433.652 | 337.948
3.92 | 1436.439 | 342.747 |  |  |  | 3.92 | 1370.109 | 336.665
3.94 | 1393.652 | 347.74 |  |  |  | 3.94 | 1338.338 | 349.503
3.96 | 1308.078 | 353.471 |  |  |  | 3.96 | 1274.795 | 346.056
3.98 | 1308.078 | 352.849 |  |  |  | 3.98 | 1306.567 | 345.12
4 | 1350.865 | 347.688 |  |  |  | 4 | 1306.567 | 346.549
4.02 | 1436.439 | 348.008 |  |  |  | 4.02 | 1401.88 | 330.909
4.04 | 1928.493 | 307.656 |  |  |  | 4.04 | 2672.733 | 307.353
4.06 | 1308.078 | 349.27 |  |  |  | 4.06 | 1274.795 | 342.258
4.08 | 1222.503 | 361.602 |  |  |  | 4.08 | 1243.024 | 355.35
4.1 | 1393.652 | 353.952 |  |  |  | 4.1 | 1306.567 | 346.519
4.12 | 1393.652 | 345.087 |  |  |  | 4.12 | 1433.652 | 343.877
4.14 | 1265.29 | 353.756 |  |  |  | 4.14 | 1306.567 | 349.867
4.16 | 1222.503 | 360.755 |  |  |  | 4.16 | 1211.253 | 367.363
4.18 | 1393.652 | 361.222 |  |  |  | 4.18 | 1274.795 | 361.417
4.2 | 1308.078 | 362.702 |  |  |  | 4.2 | 1243.024 | 357.22
4.22 | 1222.503 | 364.484 |  |  |  | 4.22 | 1147.71 | 364.299
4.24 | 1222.503 | 362.458 |  |  |  | 4.24 | 1179.481 | 362.757
4.26 | 1222.503 | 365.868 |  |  |  | 4.26 | 1179.481 | 358.598
4.28 | 1051.354 | 376.289 |  |  |  | 4.28 | 1020.625 | 375.006
4.3 | 1051.354 | 381.487 |  |  |  | 4.3 | 1020.625 | 380.356
4.32 | 965.78 | 381.113 |  |  |  | 4.32 | 988.853 | 367.614
4.34 | 1051.354 | 378.568 |  |  |  | 4.34 | 988.853 | 382.31
4.36 | 1136.929 | 374.698 |  |  |  | 4.36 | 1052.396 | 362.394
4.38 | 1735.95 | 345.259 |  |  |  | 4.38 | 2418.562 | 338.189
4.4 | 1265.29 | 354.147 |  |  |  | 4.4 | 2100.849 | 352.179
4.42 | 1094.141 | 371.464 |  |  |  | 4.42 | 1052.396 | 366.717
4.44 | 1094.141 | 376.166 |  |  |  | 4.44 | 1052.396 | 371.61
4.46 | 1136.929 | 379.701 |  |  |  | 4.46 | 1020.625 | 378.987
4.48 | 1094.141 | 379.384 |  |  |  | 4.48 | 1084.167 | 373.487
4.5 | 1179.716 | 373.017 |  |  |  | 4.5 | 1084.167 | 364.142
4.52 | 1222.503 | 368.901 |  |  |  | 4.52 | 1147.71 | 360.743
4.54 | 1051.354 | 369.511 |  |  |  | 4.54 | 1052.396 | 362.613
4.56 | 1136.929 | 374.545 |  |  |  | 4.56 | 1115.939 | 373.995
4.58 | 1008.567 | 382.042 |  |  |  | 4.58 | 957.082 | 384.858
4.6 | 880.205 | 392.14 |  |  |  | 4.6 | 861.768 | 395.488
4.62 | 880.205 | 404.151 |  |  |  | 4.62 | 829.997 | 404.921
4.64 | 666.269 | 432.291 |  |  |  | 4.64 | 798.226 | 434.023

## Test-2200
Report number | K-656038-001 R00
Prepared for | Test Products Incorporated
Issue Date | 2023-November-24
Citation | W. Cantor, S. Marri, and L. Gordon, “NFPA 70E proposed dc arc flash updated guidance,” in 2024 IEEE IAS Electrical Safety Workshop (ESW), 2024, pp. 160–211. [Online].
Test Number | 23-2200
Scenario | 480V - 20kA Available Arc on battery side of breaker with Cabinet w/ Mannequin A: calorimeter at 18", 66" high, breaker terminals : B: calorimeter at 6", 74" high, angled to breaker terminals
Test Voltage (V) | 434.9
Arc Current (A) | 10870
Arc Voltage (V) | 264.9
Duration of Arc (s) | 0.1016
Arc Energy (kJ) | 261.4 |  | Notes
Incident Energy at 18" distance (cal/cm²) | 1.32 |  | Test 23-2200 was taken inside of the battery cabinet at highest voltage and highest current. Connections were made by replacing the spare circuit breaker with a Kinectrics provided breaker. The Kinectrics provided circuit breaker was similar in profile/dimensions to that provided by TPI. Additionally, a mannequin was installed with the arm away from terminals of the circuit breaker. The voltage was achieved as per Test 23-2178, and the current was approximately achieved. Only a quick spark was observed, but black smoke followed by a fire near the terminals of the circuit breaker pursued. As a result, the circuit breaker could no longer be used. Review of high speed video shows the arc grow just above the calorimeter placed in front of the battery cabinet, before turning into flames and extinguishing. This concluded the test program.
Electrode Gap (mm) | 36.4
Final Electrode Gap (mm) | 36.4 |  |  | I | Vbat
Configuration | closed parallel |  |  | 0 | 480
|  |  |  | 20000 | 0 | Incident Energy at 6" distance (cal/cm²) | 6.7
A: calorimeter at 18" | [5 empty] | B: calorimeter at 6"
Time (s) | Current (A) | Voltage (V) |  |  |  | Time (s) | Current (A) | Voltage (V)
0.109 | 2975.759 | 51.084 |  |  |  | 0.109 | 1328.915 | 38.708
0.11 | 8254.251 | 100.113 |  |  |  | 0.11 | 5116.296 | 86.958
0.111 | 11746.284 | 153.856 |  |  |  | 0.111 | 10039.823 | 146.628
0.112 | 13362.897 | 198.378 |  |  |  | 0.112 | 12580.368 | 205.868
0.116 | 13059.225 | 213.016 |  |  |  | 0.117 | 13001.688 | 220.013
0.118 | 12692.851 | 212.226 |  |  |  | 0.121 | 13705.458 | 213.957
0.121 | 13528.923 | 212.09 |  |  |  | 0.124 | 12907.63 | 220.217
0.126 | 12822.096 | 208.045 |  |  |  | 0.128 | 13383.832 | 209.122
0.127 | 13393.018 | 207.068 |  |  |  | 0.133 | 13693.909 | 203.991
0.132 | 13750.632 | 203.901 |  |  |  | 0.137 | 13518.913 | 214.426
0.137 | 13647.307 | 215.604 |  |  |  | 0.14 | 13307.607 | 228.903
0.139 | 13319.815 | 224.585 |  |  |  | 0.142 | 12542.856 | 243.996
0.14 | 12932.08 | 229.894 |  |  |  | 0.144 | 11667.232 | 241.058
0.141 | 12544.345 | 233.13 |  |  |  | 0.148 | 12352.061 | 226.966
0.142 | 12272.895 | 233.542 |  |  |  | 0.15 | 12956.507 | 208.74
0.144 | 11857.139 | 234.573 |  |  |  | 0.156 | 13596.155 | 217.719
0.148 | 12378.678 | 216.985 |  |  |  | 0.161 | 12690.041 | 218.242
0.15 | 13001.082 | 211.826 |  |  |  | 0.165 | 13342.809 | 218.746
0.153 | 13188.47 | 213.728 |  |  |  | 0.169 | 12722.102 | 220.262
0.155 | 13554.843 | 215.461 |  |  |  | 0.172 | 13427.443 | 221.954
0.159 | 12992.323 | 217.248 |  |  |  | 0.175 | 12347.903 | 225.971
0.164 | 13246.612 | 216.19 |  |  |  | 0.178 | 12926.017 | 228.927
0.167 | 12742.234 | 217.613 |  |  |  | 0.183 | 12652.713 | 233.262
0.172 | 13272.533 | 220.675 |  |  |  | 0.187 | 12121.352 | 253.784
0.174 | 12888.998 | 223.318 |  |  |  | 0.189 | 11520.602 | 277.664
0.176 | 12503.364 | 224.996 |  |  |  | 0.19 | 10832.076 | 296.814
0.182 | 12716.672 | 227.702 |  |  |  | 0.191 | 9806.126 | 315.489
0.187 | 12113.528 | 253.461 |  |  |  | 0.192 | 8780.176 | 317.522
0.189 | 11445.583 | 287.947 |  |  |  | 0.193 | 8203.078 | 327.943
0.19 | 10670.113 | 307.033 |  |  |  | 0.194 | 7561.859 | 338.147
0.191 | 9427.584 | 318.146 |  |  |  | 0.198 | 6951.131 | 359.855
0.192 | 8150.015 | 328.627 |  |  |  | 0.2 | 6265.747 | 380.994
0.194 | 7589.954 | 345.115 |  |  |  | 0.202 | 5433.733 | 402.666
0.197 | 6930.768 | 350.852 |  |  |  | 0.203 | 4612.252 | 421.407
0.2 | 6254.422 | 377.35 |  |  |  | 0.205 | 3522.18 | 439.433
0.202 | 5170.721 | 407.185 |  |  |  | 0.207 | 2471.006 | 457.398
0.203 | 4240.444 | 422.504 |  |  |  | 0.21 | 1219.058 | 470.847
0.204 | 3755.685 | 450.588 |  |  |  | 0.214 | 1922.828 | 479.954
0.206 | 2981.266 | 441.81 |  |  |  | 0.216 | 903.715 | 498.745
0.208 | 2055.881 | 453.13
0.21 | 1379.534 | 452.759
0.213 | 1817.01 | 474.079
0.215 | 1319.292 | 494.495
0.216 | 750.47 | 515.165