## DELETE (hidden)
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Test Number | 7265
Scenario | 6mm gap with box
Test Voltage (V)
Arc Current (A)
Arc Voltage (V)
Duration of Arc (s)
Arc Energy (kJ)
Incident Energy at 450 mm Distance (cal/cm²)
Electrode Gap (mm)
Final Electrode Gap (mm)
Configuration | inline
Time (s) | Current (A) | Voltage (V)

## Test-7258
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7258
Scenario | 105 V - 7 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 105
Arc Current (A) | 2882
Arc Voltage (V) | 64.68
Duration of Arc (s) | 0.0439
Arc Energy (kJ) | 8.123
Incident Energy at 450 mm Distance (cal/cm²) | 0.03
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 105
0.075 | 26.681 | 0.81 | 7000 | 0
0.076 | 125.505 | 1.088
0.077 | 645.987 | 8.575
0.078 | 1526.57 | 28.781
0.079 | 2281.04 | 40.758
0.08 | 2847.013 | 44.075
0.081 | 3239.179 | 47.9
0.082 | 3563.387 | 51.557
0.083 | 3786.117 | 51.931
0.084 | 3930.023 | 51.623
0.085 | 4089.099 | 52.634
0.086 | 4152.27 | 53.884
0.087 | 4152.143 | 56.106
0.088 | 4147.898 | 57.653
0.089 | 4097.731 | 57.165
0.09 | 4069.778 | 57.285
0.091 | 4092.06 | 58.39
0.092 | 4053.32 | 59.419
0.093 | 3999.49 | 60.385
0.094 | 3967.28 | 60.395
0.095 | 3887.819 | 60.398
0.096 | 3863.048 | 59.945
0.097 | 3845.977 | 59.998
0.098 | 3795.194 | 62.026
0.099 | 3779.758 | 62.824
0.1 | 3743.231 | 62.607
0.101 | 3719.03 | 61.243
0.102 | 3768.95 | 59.807
0.103 | 3743.202 | 61.652
0.104 | 3670.2 | 65.766
0.105 | 3551.445 | 69.255
0.106 | 3391.695 | 71.26
0.107 | 3248.196 | 74.385
0.108 | 3081.399 | 76.757
0.109 | 2928.834 | 78.595
0.11 | 2822.221 | 80.406
0.111 | 2613.747 | 85.537
0.112 | 2294.369 | 98.607
0.113 | 1771.355 | 115.662
0.114 | 1128.161 | 122.537
0.115 | 754.553 | 108.86
0.116 | 704.99 | 95.289
0.117 | 785.124 | 93.626
0.118 | 751.162 | 103.459
0.119 | 469.079 | 119.173

## Test-7259
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7259
Scenario | 105 V - 7 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 105.5
Arc Current (A) | 3377
Arc Voltage (V) | 63.58
Duration of Arc (s) | 0.06045
Arc Energy (kJ) | 12.96
Incident Energy at 450 mm Distance (cal/cm²) | 0.05
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 105
0.079 | 2076.328 | 23.439 | 7000 | 0
0.08 | 3045.663 | 44.829
0.081 | 3450.002 | 50.63
0.082 | 3695.052 | 50.992
0.083 | 3922.776 | 50.267
0.084 | 4077.453 | 50.267
0.085 | 4197.201 | 50.63
0.086 | 4336.499 | 51.718
0.087 | 4373.694 | 52.443
0.088 | 4346.05 | 53.893
0.089 | 4371.968 | 54.618
0.09 | 4319.571 | 54.618
0.091 | 4287.882 | 55.343
0.092 | 4308.562 | 57.518
0.093 | 4246.088 | 60.419
0.094 | 4184.752 | 61.144
0.095 | 4095.595 | 60.419
0.096 | 3961.98 | 61.144
0.097 | 3901.582 | 62.594
0.098 | 3820.125 | 62.594
0.099 | 3755.914 | 63.319
0.1 | 3730.063 | 63.682
0.101 | 3667.579 | 64.769
0.102 | 3616.952 | 66.219
0.103 | 3567.688 | 64.769
0.104 | 3479.339 | 64.044
0.105 | 3461.446 | 63.319
0.106 | 3444.886 | 64.769
0.107 | 3424.633 | 65.494
0.108 | 3424.558 | 64.769
0.109 | 3389.1 | 64.044
0.11 | 3394.358 | 62.594
0.111 | 3430.87 | 59.694
0.112 | 3462.382 | 58.968
0.113 | 3514.25 | 58.243
0.114 | 3595.297 | 59.694
0.115 | 3608.62 | 62.594
0.116 | 3636.958 | 61.869
0.117 | 3645.555 | 61.869
0.118 | 3645.562 | 64.044
0.119 | 3646.175 | 65.494
0.12 | 3588.084 | 66.219
0.121 | 3484.966 | 67.67
0.122 | 3425.28 | 68.395
0.123 | 3329.941 | 68.395
0.124 | 3274.01 | 68.395
0.125 | 3234.661 | 68.395
0.126 | 3177.882 | 69.12
0.127 | 3166.614 | 70.57
0.128 | 3114.418 | 72.02
0.129 | 3014.343 | 74.196
0.13 | 2930.929 | 74.921
0.131 | 2818.832 | 75.646
0.132 | 2735.684 | 77.096
0.133 | 2685.515 | 79.996
0.134 | 2563.185 | 85.072
0.135 | 2430.866 | 92.088
0.136 | 2242.109 | 99.937
0.137 | 1970.051 | 119.335
0.138 | 1537.166 | 133.654
0.139 | 756.701 | 116.614
0.14 | 232.605 | 106.825

## Test-7260
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7260
Scenario | 105 V - 7 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 104.2
Arc Current (A) | 1974
Arc Voltage (V) | 83.43
Duration of Arc (s) | 0.08431
Arc Energy (kJ) | 12.56
Incident Energy at 450 mm Distance (cal/cm²) | 0.06
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline |  | I | Vbat
|  |  | 0 | 105
Time (s) | Current (A) | Voltage (V) | 7000 | 0
0.079 | 806.45 | 10.276
0.08 | 2003.576 | 25.736
0.081 | 2892.067 | 37.574
0.082 | 3490.63 | 43.982
0.083 | 3883.437 | 46.607
0.084 | 4201.423 | 49.806
0.085 | 4425.884 | 54.667
0.086 | 4519.41 | 58.801
0.087 | 4519.41 | 58.399
0.088 | 4444.589 | 57.689
0.089 | 4294.949 | 59.314
0.09 | 4257.539 | 62.946
0.091 | 4145.308 | 65.686
0.092 | 4014.372 | 66.519
0.093 | 3920.847 | 67.265
0.094 | 3771.206 | 68.505
0.095 | 3658.976 | 69.991
0.096 | 3584.155 | 71.655
0.097 | 3397.105 | 73.943
0.098 | 3247.464 | 76.415
0.099 | 3097.823 | 78.226
0.1 | 2948.182 | 78.972
0.101 | 2817.247 | 79.947
0.102 | 2686.311 | 81.867
0.103 | 2611.491 | 83.502
0.104 | 2443.145 | 84.228
0.105 | 2274.799 | 84.882
0.106 | 2199.979 | 86.015
0.107 | 2050.338 | 87.057
0.108 | 1975.518 | 87.295
0.109 | 1863.287 | 86.289
0.11 | 1788.467 | 84.78
0.111 | 1751.057 | 84.643
0.112 | 1788.467 | 86.777
0.113 | 1751.057 | 90.541
0.114 | 1713.647 | 94.305
0.115 | 1545.301 | 97.958
0.116 | 1376.955 | 98.921
0.117 | 1246.02 | 98.346
0.118 | 1115.084 | 97.623
0.119 | 1002.853 | 98
0.12 | 928.033 | 98.358
0.121 | 853.213 | 99.577
0.122 | 815.803 | 99.627
0.123 | 703.572 | 98.386
0.124 | 703.572 | 96.297
0.125 | 703.572 | 94.373
0.126 | 703.572 | 92.359
0.127 | 778.392 | 89.694
0.128 | 890.623 | 86.761
0.129 | 965.443 | 83.52
0.13 | 1096.379 | 80.052
0.131 | 1302.135 | 79.209
0.132 | 1470.481 | 81.229
0.133 | 1601.416 | 84.811
0.134 | 1676.237 | 86.542
0.135 | 1638.826 | 86.819
0.136 | 1638.826 | 86.212
0.137 | 1638.826 | 84.883
0.138 | 1601.416 | 83.001
0.139 | 1638.826 | 82.25
0.14 | 1676.237 | 86.643
0.141 | 1751.057 | 93.986
0.142 | 1657.532 | 97.363
0.143 | 1414.365 | 86.205
0.144 | 1302.135 | 80.469
0.145 | 1433.07 | 82.46
0.146 | 1564.006 | 87.922
0.147 | 1638.826 | 90.557
0.148 | 1526.596 | 87.959
0.149 | 1451.776 | 82.514
0.15 | 1489.186 | 82.549
0.151 | 1638.826 | 93.011
0.152 | 1638.826 | 104.158
0.153 | 1414.365 | 96.5
0.154 | 1096.379 | 72.908
0.155 | 1246.02 | 66.67
0.156 | 1545.301 | 74.597
0.157 | 1844.582 | 84.912
0.158 | 1938.108 | 95.177
0.159 | 1788.467 | 104.197
0.16 | 1526.596 | 106.909
0.161 | 1189.904 | 105.997
0.162 | 928.033 | 111.079
0.163 | 722.277 | 117.003
0.164 | 404.291 | 115.255

## Test-7261
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7261
Scenario | 105 V - 7 kA Available - 3mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 106.3
Arc Current (A) | 3974
Arc Voltage (V) | 58.18
Duration of Arc (s) | 0.3256
Arc Energy (kJ) | 72.57
Incident Energy at 450 mm Distance (cal/cm²) | 0.24
Electrode Gap (mm) | 3
Final Electrode Gap (mm) | -
Configuration | inline |  | I | Vbat
|  |  | 0 | 105
Time (s) | Current (A) | Voltage (V) | 7000 | 0
0.083 | 787.953 | 42.539
0.084 | 1291.545 | 43.89
0.085 | 2077.639 | 44.881
0.086 | 2519.818 | 44.143
0.087 | 2980.42 | 41.705
0.088 | 3348.902 | 39.307
0.089 | 3791.08 | 37.715
0.09 | 4030.593 | 37.77
0.091 | 4233.258 | 38.616
0.092 | 4528.044 | 39.395
0.093 | 4859.678 | 40.672
0.094 | 4896.526 | 42.757
0.095 | 5117.615 | 44.999
0.096 | 5283.432 | 46.598
0.097 | 5191.311 | 48.489
0.098 | 5375.552 | 50.024
0.099 | 5412.4 | 51.447
0.1 | 5228.16 | 52.317
0.101 | 5320.28 | 51.976
0.102 | 5136.039 | 50.347
0.103 | 4933.374 | 48.41
0.104 | 4970.222 | 48.146
0.105 | 4712.285 | 48.58
0.106 | 4693.861 | 49.211
0.107 | 4785.981 | 49.089
0.108 | 4712.285 | 48.468
0.109 | 4822.829 | 48.55
0.11 | 4822.829 | 49.747
0.111 | 4638.589 | 50.55
0.112 | 4785.981 | 50.3
0.113 | 4712.285 | 49.772
0.114 | 4712.285 | 48.88
0.115 | 4822.829 | 47.546
0.116 | 4693.861 | 46.97
0.117 | 4712.285 | 47.079
0.118 | 4785.981 | 47.772
0.119 | 4601.74 | 48.07
0.12 | 4749.133 | 47.508
0.121 | 4785.981 | 46.655
0.122 | 4675.437 | 45.836
0.123 | 4878.102 | 45.591
0.124 | 4822.829 | 45.238
0.125 | 4804.405 | 44.82
0.126 | 4970.222 | 44.827
0.127 | 4914.95 | 44.925
0.128 | 4914.95 | 45.297
0.129 | 5043.919 | 46.234
0.13 | 4914.95 | 46.379
0.131 | 5007.07 | 45.092
0.132 | 5154.463 | 43.415
0.133 | 4970.222 | 42.254
0.134 | 5099.191 | 42.064
0.135 | 5117.615 | 42.394
0.136 | 4933.374 | 43.21
0.137 | 5136.039 | 43.381
0.138 | 5117.615 | 43.583
0.139 | 5099.191 | 44.086
0.14 | 5283.432 | 45.173
0.141 | 5246.584 | 46.336
0.142 | 5246.584 | 46.825
0.143 | 5393.976 | 45.974
0.144 | 5209.735 | 45.055
0.145 | 5154.463 | 45.932
0.146 | 5209.735 | 48.782
0.147 | 4988.646 | 50.847
0.148 | 5136.039 | 52.226
0.149 | 5136.039 | 52.556
0.15 | 5007.07 | 52.424
0.151 | 5117.615 | 52.178
0.152 | 4914.95 | 52.727
0.153 | 4712.285 | 53.361
0.154 | 4730.709 | 53.707
0.155 | 4528.044 | 52.99
0.156 | 4620.164 | 52.233
0.157 | 4583.316 | 52.752
0.158 | 4491.196 | 52.973
0.159 | 4564.892 | 52.561
0.16 | 4509.62 | 51.655
0.161 | 4417.499 | 51.649
0.162 | 4509.62 | 50.527
0.163 | 4343.803 | 50.161
0.164 | 4454.348 | 51.874
0.165 | 4564.892 | 55.683
0.166 | 4417.499 | 57.533
0.167 | 4583.316 | 57.348
0.168 | 4620.164 | 57.135
0.169 | 4435.923 | 57.218
0.17 | 4454.348 | 57.767
0.171 | 4306.955 | 57.862
0.172 | 4177.986 | 57.596
0.173 | 4306.955 | 57.331
0.174 | 4141.138 | 57.289
0.175 | 4159.562 | 57.199
0.176 | 4159.562 | 57.693
0.177 | 4012.169 | 57.406
0.178 | 4085.866 | 57.032
0.179 | 4049.017 | 57.064
0.18 | 3938.473 | 58.373
0.181 | 4085.866 | 58.705
0.182 | 4030.593 | 56.337
0.183 | 4012.169 | 48.096
0.184 | 4122.714 | 43.327
0.185 | 3956.897 | 44.9
0.186 | 3938.473 | 46.55
0.187 | 4067.442 | 48.934
0.188 | 4177.986 | 51.949
0.189 | 4472.772 | 52.116
0.19 | 4638.589 | 51.411
0.191 | 4601.74 | 51.228
0.192 | 4712.285 | 51.34
0.193 | 4675.437 | 51.297
0.194 | 4491.196 | 50.596
0.195 | 4601.74 | 49.582
0.196 | 4583.316 | 48.9
0.197 | 4472.772 | 48.846
0.198 | 4638.589 | 48.426
0.199 | 4546.468 | 47.561
0.2 | 4601.74 | 45.563
0.201 | 4785.981 | 43.945
0.202 | 4620.164 | 43.19
0.203 | 4675.437 | 42.955
0.204 | 4785.981 | 42.951
0.205 | 4675.437 | 43.232
0.206 | 4914.95 | 43.949
0.207 | 5043.919 | 44.771
0.208 | 5007.07 | 46.624
0.209 | 5172.887 | 48.326
0.21 | 5209.735 | 49.674
0.211 | 5043.919 | 49.597
0.212 | 5191.311 | 49.318
0.213 | 5062.343 | 49.419
0.214 | 4933.374 | 50.021
0.215 | 5043.919 | 50.572
0.216 | 4878.102 | 51.28
0.217 | 4878.102 | 51.658
0.218 | 4896.526 | 53.179
0.219 | 4693.861 | 54.263
0.22 | 4730.709 | 54.659
0.221 | 4693.861 | 54.548
0.222 | 4528.044 | 55.684
0.223 | 4675.437 | 58.283
0.224 | 4509.62 | 58.758
0.225 | 4472.772 | 58.862
0.226 | 4528.044 | 60.143
0.227 | 4325.379 | 61.567
0.228 | 4233.258 | 60.996
0.229 | 4177.986 | 59.539
0.23 | 4012.169 | 60.03
0.231 | 4049.017 | 61.95
0.232 | 3901.625 | 62.636
0.233 | 3901.625 | 62.14
0.234 | 3956.897 | 62.322
0.235 | 3754.232 | 62.308
0.236 | 3754.232 | 61.917
0.237 | 3754.232 | 62.53
0.238 | 3606.839 | 63.954
0.239 | 3717.384 | 65.476
0.24 | 3680.536 | 66.585
0.241 | 3643.687 | 63.607
0.242 | 3717.384 | 62.488
0.243 | 3569.991 | 62.059
0.244 | 3459.446 | 62.536
0.245 | 3496.295 | 64.351
0.246 | 3422.598 | 66.652
0.247 | 3533.143 | 66.881
0.248 | 3569.991 | 63.286
0.249 | 3459.446 | 63.886
0.25 | 3533.143 | 64.982
0.251 | 3385.75 | 66.465
0.252 | 3367.326 | 68.418
0.253 | 3459.446 | 70.731
0.254 | 3330.478 | 72.364
0.255 | 3348.902 | 71.229
0.256 | 3348.902 | 69.921
0.257 | 3201.509 | 69.948
0.258 | 3164.661 | 70.715
0.259 | 3054.116 | 72.652
0.26 | 2980.42 | 74.178
0.261 | 3054.116 | 75.115
0.262 | 2925.148 | 75.349
0.263 | 2906.724 | 75.306
0.264 | 2869.875 | 75.489
0.265 | 2722.483 | 76.581
0.266 | 2759.331 | 78.286
0.267 | 2648.786 | 80.367
0.268 | 2575.09 | 82.828
0.269 | 2611.938 | 86.279
0.27 | 2446.121 | 89.42
0.271 | 2354.001 | 77.513
0.272 | 2280.304 | 73.175
0.273 | 2059.215 | 72.57
0.274 | 1985.519 | 72.235
0.275 | 2022.367 | 72.235
0.276 | 2132.912 | 72.916
0.277 | 2280.304 | 73.208
0.278 | 2317.153 | 73.28
0.279 | 2409.273 | 73.565
0.28 | 2501.394 | 74.291
0.281 | 2464.545 | 76.44
0.282 | 2538.242 | 79.782
0.283 | 2611.938 | 82.538
0.284 | 2501.394 | 65.238
0.285 | 2501.394 | 57.152
0.286 | 2317.153 | 53.238
0.287 | 2077.639 | 46.361
0.288 | 2409.273 | 43.173
0.289 | 2722.483 | 41.661
0.29 | 2961.996 | 41.057
0.291 | 3367.326 | 40.909
0.292 | 3772.656 | 40.786
0.293 | 3975.321 | 40.244
0.294 | 4251.683 | 39.597
0.295 | 4528.044 | 39.066
0.296 | 4675.437 | 39.368
0.297 | 4841.254 | 41.119
0.298 | 5043.919 | 43.106
0.299 | 5154.463 | 44.345
0.3 | 5246.584 | 45.106
0.301 | 5430.825 | 45.903
0.302 | 5375.552 | 47.453
0.303 | 5228.16 | 50.007
0.304 | 5357.128 | 55.084
0.305 | 5154.463 | 60.899
0.306 | 5191.311 | 63.977
0.307 | 5172.887 | 67.882
0.308 | 4970.222 | 69.569
0.309 | 4933.374 | 66.259
0.31 | 4564.892 | 62.033
0.311 | 4159.562 | 62.082
0.312 | 3938.473 | 62.113
0.313 | 3606.839 | 61.725
0.314 | 3717.384 | 61.258
0.315 | 3662.112 | 62.124
0.316 | 3606.839 | 62.582
0.317 | 3717.384 | 61.849
0.318 | 3588.415 | 61.286
0.319 | 3606.839 | 61.83
0.32 | 3643.687 | 61.674
0.321 | 3496.295 | 58.066
0.322 | 3625.263 | 53.632
0.323 | 3643.687 | 53.856
0.324 | 3569.991 | 53.832
0.325 | 3717.384 | 53.408
0.326 | 3827.928 | 53.347
0.327 | 3827.928 | 54.081
0.328 | 4012.169 | 54.494
0.329 | 4030.593 | 55.416
0.33 | 4049.017 | 56.686
0.331 | 4233.258 | 57.989
0.332 | 4159.562 | 59.086
0.333 | 4177.986 | 59.933
0.334 | 4270.107 | 59.677
0.335 | 4122.714 | 59.853
0.336 | 4049.017 | 59.559
0.337 | 4049.017 | 60.1
0.338 | 3864.777 | 60.633
0.339 | 3975.321 | 61.022
0.34 | 3938.473 | 61.677
0.341 | 3827.928 | 63.405
0.342 | 3975.321 | 64.571
0.343 | 3827.928 | 65.668
0.344 | 3791.08 | 66.272
0.345 | 3772.656 | 67.383
0.346 | 3606.839 | 67.646
0.347 | 3625.263 | 66.425
0.348 | 3569.991 | 66.073
0.349 | 3422.598 | 65.936
0.35 | 3459.446 | 65.164
0.351 | 3312.054 | 66.683
0.352 | 3275.206 | 67.714
0.353 | 3312.054 | 68.823
0.354 | 3238.357 | 69.795
0.355 | 3312.054 | 69.207
0.356 | 3275.206 | 68.793
0.357 | 3164.661 | 69.329
0.358 | 3201.509 | 70.143
0.359 | 3090.965 | 70.591
0.36 | 3054.116 | 70.486
0.361 | 3127.813 | 69.8
0.362 | 2980.42 | 69.161
0.363 | 2980.42 | 69.12
0.364 | 3017.268 | 69.033
0.365 | 2906.724 | 68.984
0.366 | 2998.844 | 68.206
0.367 | 3017.268 | 66.671
0.368 | 2906.724 | 63.1
0.369 | 3017.268 | 59.2
0.37 | 2943.572 | 55.531
0.371 | 2980.42 | 54.433
0.372 | 3109.389 | 87.411
0.373 | 3201.509 | 91.075
0.374 | 3385.75 | 85.291
0.375 | 3367.326 | 81.497
0.376 | 3330.478 | 73.769
0.377 | 2759.331 | 64.52
0.378 | 2482.969 | 60.44
0.379 | 2354.001 | 56.96
0.38 | 2427.697 | 50.5
0.381 | 2611.938 | 43.783
0.382 | 2833.027 | 41.786
0.383 | 3090.965 | 42.598
0.384 | 3348.902 | 43.75
0.385 | 3588.415 | 45.403
0.386 | 4012.169 | 46.579
0.387 | 4233.258 | 47.682
0.388 | 4362.227 | 49.7
0.389 | 4620.164 | 52.766
0.39 | 4785.981 | 57.276
0.391 | 4675.437 | 60.11
0.392 | 4841.254 | 61.335
0.393 | 4804.405 | 66.262
0.394 | 4601.74 | 69.832
0.395 | 4491.196 | 66.885
0.396 | 4251.683 | 67.449
0.397 | 3956.897 | 70.294
0.398 | 3643.687 | 76.296
0.399 | 3459.446 | 87.504
0.4 | 3533.143 | 78.499
0.401 | 3330.478 | 81.074
0.402 | 3035.692 | 96.255
0.403 | 2648.786 | 130.752
0.404 | 2501.394 | 124.046
0.405 | 2427.697 | 120.122
0.406 | 2040.791 | 122.67
0.407 | 1224 | 113.854
0.408 | 658.984 | 113.206
0.409 | 345.775 | 103.681

## Test-7262
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7262
Scenario | 105 V - 7 kA Available - 3mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 106
Arc Current (A) | 4001
Arc Voltage (V) | 57.48
Duration of Arc (s) | 0.2858
Arc Energy (kJ) | 63.09
Incident Energy at 450 mm Distance (cal/cm²) | 0.24
Electrode Gap (mm) | 3
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 105
0.081 | 651.608 | 2.732 | 7000 | 0
0.082 | 1651.749 | 22.246
0.083 | 2272.717 | 39.762
0.084 | 2771.086 | 42.205
0.085 | 3321.051 | 41.018
0.086 | 3809.043 | 40.308
0.087 | 4138.164 | 38.886
0.088 | 4491.279 | 37.188
0.089 | 4836.677 | 36.099
0.09 | 5026.298 | 35.927
0.091 | 5186.739 | 36.699
0.092 | 5369.582 | 37.889
0.093 | 5404.879 | 38.739
0.094 | 5454.107 | 39.697
0.095 | 5554.989 | 40.938
0.096 | 5531.222 | 42.377
0.097 | 5503.172 | 43.978
0.098 | 5480.024 | 45.449
0.099 | 5322.15 | 45.899
0.1 | 5256.327 | 45.189
0.101 | 5210.374 | 45.101
0.102 | 5178.232 | 46.339
0.103 | 5169.782 | 47.81
0.104 | 5115.001 | 48.536
0.105 | 5077.557 | 48.143
0.106 | 5073.834 | 46.929
0.107 | 5048.678 | 45.825
0.108 | 5040.836 | 45.429
0.109 | 5053.849 | 45.512
0.11 | 5040.493 | 45.99
0.111 | 5067.843 | 46.292
0.112 | 5082.001 | 46.488
0.113 | 5080.285 | 46.18
0.114 | 5104.219 | 45.965
0.115 | 5079.133 | 45.365
0.116 | 5048.869 | 45.971
0.117 | 5042.523 | 45.877
0.118 | 5045.92 | 45.162
0.119 | 5085.959 | 44.449
0.12 | 5165.47 | 44.853
0.121 | 5147.951 | 45.7
0.122 | 5165.183 | 45.424
0.123 | 5167.96 | 45.738
0.124 | 5112.062 | 45.891
0.125 | 5095.311 | 46.328
0.126 | 5074.243 | 46.283
0.127 | 5063.388 | 46.212
0.128 | 5079.581 | 46.536
0.129 | 5075.699 | 46.224
0.13 | 5073.722 | 46.117
0.131 | 5100.241 | 46.268
0.132 | 5034.692 | 46.616
0.133 | 5004.811 | 47.509
0.134 | 4978.389 | 47.763
0.135 | 4950.069 | 48.007
0.136 | 4962.763 | 48.087
0.137 | 4967.72 | 48.214
0.138 | 4961.412 | 48.087
0.139 | 4971.833 | 48.559
0.14 | 4911.674 | 49.972
0.141 | 4833.865 | 50.754
0.142 | 4795.565 | 50.213
0.143 | 4787.571 | 48.115
0.144 | 4820.085 | 46.796
0.145 | 4878.626 | 47.045
0.146 | 4895.783 | 47.667
0.147 | 4919.936 | 47.825
0.148 | 4924.054 | 47.301
0.149 | 4908.128 | 46.94
0.15 | 4910.557 | 46.719
0.151 | 4913.219 | 46.892
0.152 | 4914.915 | 47.859
0.153 | 4938.31 | 48.511
0.154 | 4948.711 | 47.31
0.155 | 4966.51 | 45.346
0.156 | 5063.131 | 44.043
0.157 | 5066.383 | 43.117
0.158 | 5110.417 | 42.509
0.159 | 5170.234 | 41.943
0.16 | 5204.105 | 41.649
0.161 | 5285.912 | 41.23
0.162 | 5351.48 | 41.434
0.163 | 5380.088 | 42.393
0.164 | 5394.403 | 43.793
0.165 | 5365.68 | 44.978
0.166 | 5274.648 | 45.441
0.167 | 5220.076 | 45.775
0.168 | 5188.582 | 45.221
0.169 | 5190.134 | 45.433
0.17 | 5197.798 | 46.49
0.171 | 5149.193 | 48.666
0.172 | 5077.801 | 50.675
0.173 | 4989.389 | 51.696
0.174 | 4836.554 | 52.674
0.175 | 4754.772 | 53.615
0.176 | 4640.654 | 55.423
0.177 | 4543.409 | 56.296
0.178 | 4494.659 | 56.515
0.179 | 4437.835 | 55.825
0.18 | 4405.547 | 55.259
0.181 | 4392.953 | 54.574
0.182 | 4334.506 | 54.029
0.183 | 4325.1 | 53.545
0.184 | 4326.278 | 53.348
0.185 | 4326.881 | 53.755
0.186 | 4348.464 | 53.909
0.187 | 4353.81 | 54.613
0.188 | 4355.735 | 54.032
0.189 | 4376.502 | 54.203
0.19 | 4370.037 | 53.526
0.191 | 4354.477 | 53.908
0.192 | 4350.255 | 53.692
0.193 | 4345.023 | 54.114
0.194 | 4368.622 | 54.317
0.195 | 4384.295 | 54.909
0.196 | 4361.589 | 55.852
0.197 | 4336.379 | 56.25
0.198 | 4287.379 | 56.566
0.199 | 4210.574 | 56.314
0.2 | 4185.064 | 56.572
0.201 | 4157.776 | 56.933
0.202 | 4150.235 | 56.372
0.203 | 4195.838 | 54.523
0.204 | 4264.616 | 52.602
0.205 | 4380.861 | 48.321
0.206 | 4550.275 | 46.055
0.207 | 4577.056 | 47.461
0.208 | 4643.951 | 48.066
0.209 | 4648.785 | 52.681
0.21 | 4547.741 | 56.244
0.211 | 4477.683 | 58.936
0.212 | 4370.254 | 60.275
0.213 | 4242.059 | 61.097
0.214 | 4168.789 | 61.008
0.215 | 4050.281 | 60.238
0.216 | 4009.88 | 58.506
0.217 | 3990.707 | 57.844
0.218 | 3979.052 | 58.392
0.219 | 3970.207 | 59.543
0.22 | 3966.462 | 59.177
0.221 | 3963.394 | 59.322
0.222 | 3966.177 | 59.389
0.223 | 3927.393 | 60.581
0.224 | 3870.954 | 61.109
0.225 | 3831.91 | 61.685
0.226 | 3800.586 | 60.818
0.227 | 3802.115 | 60.407
0.228 | 3829.877 | 59.354
0.229 | 3868.517 | 56.777
0.23 | 3942.813 | 56.219
0.231 | 3982.318 | 56.667
0.232 | 3984.206 | 56.149
0.233 | 4017.217 | 55.298
0.234 | 4055.89 | 55.082
0.235 | 4082.183 | 54.95
0.236 | 4180.085 | 53.106
0.237 | 4301.589 | 48.67
0.238 | 4431.597 | 47.539
0.239 | 4581.646 | 47.096
0.24 | 4631.083 | 47.035
0.241 | 4678.938 | 47.984
0.242 | 4712.03 | 49.442
0.243 | 4699.008 | 50.253
0.244 | 4699.521 | 50.866
0.245 | 4692.904 | 52.122
0.246 | 4645.31 | 53.333
0.247 | 4617.95 | 53.354
0.248 | 4578.869 | 52.346
0.249 | 4522.85 | 53.282
0.25 | 4464.259 | 55.434
0.251 | 4380.88 | 57.134
0.252 | 4294.036 | 58.454
0.253 | 4258.473 | 58.899
0.254 | 4198.743 | 59.32
0.255 | 4147.079 | 59.509
0.256 | 4108.286 | 59.911
0.257 | 4006.936 | 60.353
0.258 | 3936.456 | 62.158
0.259 | 3852.768 | 63.506
0.26 | 3750.707 | 64.584
0.261 | 3696.195 | 65.159
0.262 | 3635.217 | 65.774
0.263 | 3572.798 | 66.278
0.264 | 3531.775 | 65.577
0.265 | 3486.49 | 64.527
0.266 | 3461.791 | 64.27
0.267 | 3442.256 | 64.529
0.268 | 3423.312 | 64.662
0.269 | 3429.937 | 65.052
0.27 | 3433.019 | 65.3
0.271 | 3421.117 | 65.664
0.272 | 3426.036 | 64.984
0.273 | 3415.981 | 63.656
0.274 | 3410.885 | 63.954
0.275 | 3416.515 | 64.158
0.276 | 3427.477 | 63.224
0.277 | 3444.587 | 64.062
0.278 | 3452.698 | 64.392
0.279 | 3448.393 | 64.237
0.28 | 3468.657 | 64.361
0.281 | 3453.383 | 65.19
0.282 | 3409.739 | 65.954
0.283 | 3355.46 | 68.371
0.284 | 3323.672 | 66.727
0.285 | 3265.985 | 68.16
0.286 | 3138.053 | 78.937
0.287 | 2859.705 | 80.179
0.288 | 2824.498 | 72.757
0.289 | 2809.557 | 72.241
0.29 | 2766.474 | 74.167
0.291 | 2692.455 | 76.595
0.292 | 2609.631 | 76.708
0.293 | 2559.966 | 76.503
0.294 | 2532.638 | 76.987
0.295 | 2513.176 | 75.435
0.296 | 2539.678 | 74.006
0.297 | 2577.429 | 72.554
0.298 | 2606.127 | 71.38
0.299 | 2652.076 | 70.935
0.3 | 2686.185 | 71.566
0.301 | 2687.069 | 72.384
0.302 | 2704.204 | 72.736
0.303 | 2718.092 | 72.184
0.304 | 2744.336 | 71.635
0.305 | 2777.239 | 71.198
0.306 | 2786.381 | 70.514
0.307 | 2796.193 | 70.288
0.308 | 2823.219 | 70.357
0.309 | 2836.809 | 70.158
0.31 | 2862.72 | 69.824
0.311 | 2892.727 | 69.479
0.312 | 2924.136 | 69.158
0.313 | 2964.797 | 68.961
0.314 | 2989.004 | 68.454
0.315 | 3000.1 | 67.41
0.316 | 3044.46 | 65.925
0.317 | 3110.035 | 64.084
0.318 | 3175.272 | 62.037
0.319 | 3315.721 | 59.994
0.32 | 3448.907 | 58.075
0.321 | 3565.397 | 56.864
0.322 | 3733.281 | 55.294
0.323 | 3836.222 | 53.884
0.324 | 3915.422 | 53.487
0.325 | 4027.872 | 54.128
0.326 | 4058.039 | 54.925
0.327 | 4095.026 | 56.368
0.328 | 4111.929 | 57.903
0.329 | 4072.367 | 60.126
0.33 | 4033.789 | 60.934
0.331 | 4027.125 | 57.33
0.332 | 4036.628 | 54.277
0.333 | 4067.992 | 54.702
0.334 | 4066.436 | 57.379
0.335 | 4002.55 | 61.979
0.336 | 3929.197 | 63.954
0.337 | 3835.836 | 64.967
0.338 | 3748.621 | 65.151
0.339 | 3678.723 | 65.53
0.34 | 3584.032 | 66.169
0.341 | 3518.303 | 66.184
0.342 | 3483.283 | 64.117
0.343 | 3474.793 | 61.605
0.344 | 3631.337 | 53.789
0.345 | 3357.616 | 92.293
0.346 | 2552.195 | 111.964
0.347 | 2068.087 | 106.128
0.348 | 1911.056 | 85.678
0.349 | 2103.523 | 70.18
0.35 | 2273.535 | 66.661
0.351 | 2436.404 | 65.77
0.352 | 2632.489 | 66.348
0.353 | 2735.787 | 67.243
0.354 | 2822.75 | 68.607
0.355 | 2862.94 | 70.735
0.356 | 2805.431 | 75.059
0.357 | 2725.764 | 75.099
0.358 | 2694.328 | 73.315
0.359 | 2666.434 | 74.34
0.36 | 2596.988 | 77.489
0.361 | 2467.73 | 83.092
0.362 | 2152.31 | 97.418
0.363 | 1695.243 | 109.815
0.364 | 1001.547 | 120.389
0.365 | 512.096 | 125.072
0.366 | 257.528 | 119.507

## Test-7263
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7263
Scenario | 105 V - 7 kA Available - 3mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 106.1
Arc Current (A) | 3871
Arc Voltage (V) | 58.76
Duration of Arc (s) | 0.2137
Arc Energy (kJ) | 46.47
Incident Energy at 450 mm Distance (cal/cm²) | 0.16
Electrode Gap (mm) | 3
Final Electrode Gap (mm) | -
Configuration | inline |  | I | Vbat
|  |  | 0 | 105
Time (s) | Current (A) | Voltage (V) | 7000 | 0
0.081 | 623.492 | 1.348
0.082 | 1942.744 | 2.006
0.083 | 3200.201 | 3.92
0.084 | 4090.332 | 13.438
0.085 | 4607.002 | 34.579
0.086 | 4834.312 | 42.509
0.087 | 4932.101 | 43.295
0.088 | 5117.741 | 44.094
0.089 | 5191.145 | 45.103
0.09 | 5063.043 | 46.259
0.091 | 5080.329 | 47.42
0.092 | 5024.211 | 47.894
0.093 | 4893.269 | 47.954
0.094 | 5042.917 | 48.194
0.095 | 4986.799 | 48.514
0.096 | 4911.975 | 49.167
0.097 | 5042.917 | 49.291
0.098 | 4875.983 | 49.22
0.099 | 4799.739 | 48.884
0.1 | 4930.681 | 48.561
0.101 | 4743.621 | 48.716
0.102 | 4874.563 | 48.831
0.103 | 4911.975 | 49.551
0.104 | 4781.033 | 50.12
0.105 | 4893.269 | 50.019
0.106 | 4837.151 | 49.412
0.107 | 4706.21 | 49.113
0.108 | 4893.269 | 50.028
0.109 | 4743.621 | 51.424
0.11 | 4668.798 | 52.013
0.111 | 4781.033 | 51.06
0.112 | 4668.798 | 49.95
0.113 | 4762.327 | 50.118
0.114 | 4837.151 | 50.221
0.115 | 4631.386 | 50.757
0.116 | 4706.21 | 50.75
0.117 | 4668.798 | 50.529
0.118 | 4631.386 | 49.879
0.119 | 4762.327 | 49.616
0.12 | 4743.621 | 49.674
0.121 | 4724.915 | 50.369
0.122 | 4855.857 | 50.161
0.123 | 4687.504 | 49.948
0.124 | 4687.504 | 49.379
0.125 | 4818.445 | 49.698
0.126 | 4668.798 | 50.894
0.127 | 4743.621 | 52.272
0.128 | 4687.504 | 52.884
0.129 | 4556.562 | 51.646
0.13 | 4724.915 | 50.499
0.131 | 4706.21 | 49.392
0.132 | 4650.092 | 49.063
0.133 | 4781.033 | 48.849
0.134 | 4706.21 | 49.254
0.135 | 4724.915 | 49.454
0.136 | 4855.857 | 49.828
0.137 | 4706.21 | 49.762
0.138 | 4837.151 | 49.957
0.139 | 4874.563 | 49.566
0.14 | 4706.21 | 49.42
0.141 | 4799.739 | 49.272
0.142 | 4762.327 | 49.595
0.143 | 4706.21 | 49.581
0.144 | 4837.151 | 49.74
0.145 | 4799.739 | 50.107
0.146 | 4743.621 | 50.596
0.147 | 4855.857 | 49.984
0.148 | 4724.915 | 49.324
0.149 | 4724.915 | 48.534
0.15 | 4855.857 | 48.52
0.151 | 4706.21 | 48.098
0.152 | 4855.857 | 48.048
0.153 | 4911.975 | 47.817
0.154 | 4818.445 | 47.521
0.155 | 4986.799 | 47.123
0.156 | 4986.799 | 47.016
0.157 | 4874.563 | 47.073
0.158 | 5042.917 | 47.557
0.159 | 4930.681 | 48.811
0.16 | 4855.857 | 50.536
0.161 | 4930.681 | 51.277
0.162 | 4762.327 | 50.942
0.163 | 4855.857 | 50.318
0.164 | 4893.269 | 50.633
0.165 | 4687.504 | 51.366
0.166 | 4743.621 | 52.152
0.167 | 4631.386 | 52.39
0.168 | 4556.562 | 52.993
0.169 | 4687.504 | 53.9
0.17 | 4556.562 | 55.292
0.171 | 4481.738 | 56.238
0.172 | 4519.15 | 56.819
0.173 | 4294.678 | 56.806
0.174 | 4294.678 | 56.602
0.175 | 4332.09 | 56.201
0.176 | 4182.442 | 55.971
0.177 | 4294.678 | 55.999
0.178 | 4275.972 | 56.72
0.179 | 4182.442 | 56.975
0.18 | 4294.678 | 57.733
0.181 | 4163.736 | 57.729
0.182 | 4088.912 | 57.226
0.183 | 4182.442 | 56.264
0.184 | 4088.912 | 56.582
0.185 | 4145.03 | 57.731
0.186 | 4182.442 | 59.379
0.187 | 4032.794 | 59.995
0.188 | 4107.618 | 59.487
0.189 | 4088.912 | 58.524
0.19 | 3957.971 | 58.924
0.191 | 4032.794 | 59.819
0.192 | 3939.265 | 60.917
0.193 | 3883.147 | 62.342
0.194 | 3920.559 | 62.654
0.195 | 3770.911 | 63.069
0.196 | 3770.911 | 63.988
0.197 | 3733.499 | 65.167
0.198 | 3546.439 | 65.314
0.199 | 3583.851 | 65.957
0.2 | 3471.615 | 68.034
0.201 | 3359.379 | 67.908
0.202 | 3434.203 | 68.288
0.203 | 3284.556 | 70.03
0.204 | 3209.732 | 71.201
0.205 | 3247.144 | 70.186
0.206 | 3116.202 | 68.969
0.207 | 3134.908 | 68.05
0.208 | 3172.32 | 64.597
0.209 | 3172.32 | 61.566
0.21 | 3378.085 | 60.978
0.211 | 3471.615 | 60.391
0.212 | 3527.733 | 57.582
0.213 | 3764.523 | 53.6
0.214 | 3920.559 | 52.528
0.215 | 3939.265 | 53.343
0.216 | 4126.324 | 54.824
0.217 | 4070.206 | 56.282
0.218 | 4088.912 | 56.389
0.219 | 4219.854 | 55.357
0.22 | 4182.442 | 55.031
0.221 | 4219.854 | 55.449
0.222 | 4294.678 | 56.671
0.223 | 4126.324 | 57.419
0.224 | 4145.03 | 58.306
0.225 | 4126.324 | 59.498
0.226 | 3957.971 | 60.372
0.227 | 4032.794 | 61.18
0.228 | 3920.559 | 60.657
0.229 | 3883.147 | 59.57
0.23 | 4032.794 | 58.307
0.231 | 3939.265 | 58.516
0.232 | 3883.147 | 60.548
0.233 | 3901.853 | 61.691
0.234 | 3770.911 | 62.543
0.235 | 3770.911 | 63.502
0.236 | 3770.911 | 64.27
0.237 | 3621.263 | 65.663
0.238 | 3658.675 | 66.845
0.239 | 3546.439 | 68.565
0.24 | 3321.967 | 70.744
0.241 | 3264.43 | 72.186
0.242 | 3097.496 | 73.001
0.243 | 3060.084 | 74.365
0.244 | 2966.554 | 75.971
0.245 | 2798.2 | 77.942
0.246 | 2760.788 | 79.98
0.247 | 2555.023 | 81.934
0.248 | 2349.257 | 84.781
0.249 | 2197.48 | 87.772
0.25 | 1993.843 | 92.336
0.251 | 1769.372 | 96.331
0.252 | 1507.488 | 97.584
0.253 | 1301.722 | 95.414
0.254 | 1301.722 | 90.052
0.255 | 1208.192 | 91.395
0.256 | 1189.487 | 92.501
0.257 | 1264.31 | 87.432
0.258 | 1264.31 | 85.11
0.259 | 1376.546 | 83.81
0.26 | 1488.782 | 82.045
0.261 | 1563.606 | 80.017
0.262 | 1769.372 | 77.996
0.263 | 1937.725 | 72.586
0.264 | 2087.373 | 67.123
0.265 | 2362.285 | 64.936
0.266 | 2611.14 | 63.322
0.267 | 2760.788 | 61.677
0.268 | 3041.378 | 60.227
0.269 | 3209.732 | 59.255
0.27 | 3284.556 | 58.605
0.271 | 3527.733 | 57.998
0.272 | 3658.675 | 56.843
0.273 | 3658.675 | 56.045
0.274 | 3808.323 | 55.657
0.275 | 3920.559 | 56.491
0.276 | 3845.735 | 58.493
0.277 | 3995.383 | 60.667
0.278 | 3864.441 | 62.238
0.279 | 3770.911 | 63.735
0.28 | 3845.735 | 65.139
0.281 | 3639.969 | 66.031
0.282 | 3546.439 | 67.004
0.283 | 3471.615 | 69.452
0.284 | 3321.967 | 69.827
0.285 | 3321.967 | 69.923
0.286 | 3228.438 | 71.268
0.287 | 3097.496 | 73.351
0.288 | 3041.378 | 75.449
0.289 | 2854.318 | 78.793
0.29 | 2611.14 | 86.234
0.291 | 2168.433 | 107.662
0.292 | 1339.134 | 131.75
0.293 | 712.484 | 127.578
0.294 | 338.365 | 124.751

## Test-7264
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7264
Scenario | 105 V - 7 kA Available - 3mm gap, ceramic box, cotton T-shirt/mannequin test
Test Voltage (V) | 106.1
Arc Current (A) | 3887
Arc Voltage (V) | 58.74
Duration of Arc (s) | 0.2821
Arc Energy (kJ) | 62.92
Incident Energy at 450 mm Distance (cal/cm²) | 0.01 (t shirt)
Electrode Gap (mm) | 3
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V)
0.087 | 777.78 | 43.821
0.088 | 1037.039 | 43.106
0.089 | 1611.113 | 42.414
0.09 | 2222.224 | 42.689
0.091 | 3129.632 | 43.619
0.092 | 3537.039 | 44.606
0.093 | 3740.742 | 45.647
0.095 | 4166.668 | 47.784
0.096 | 4314.816 | 49.575
0.097 | 4592.594 | 50.652 | I | Vbat
0.098 | 4833.335 | 49.588 | 0 | 105
0.099 | 4759.261 | 48.505 | 7000 | 0
0.1 | 4962.964 | 48.194
0.101 | 4962.964 | 48.431
0.102 | 4907.409 | 48.443
0.104 | 5009.261 | 49.223
0.105 | 4833.335 | 50.453
0.106 | 4981.483 | 52.383
0.107 | 4796.298 | 53.062
0.108 | 4777.779 | 52.946
0.109 | 4851.853 | 53.128
0.11 | 4685.187 | 52.582
0.111 | 4796.298 | 52.364
0.112 | 4870.372 | 51.82
0.113 | 4759.261 | 52.415
0.114 | 4833.335 | 54.03
0.115 | 4722.224 | 54.845
0.116 | 4537.038 | 54.709
0.117 | 4648.15 | 54.191
0.118 | 4518.52 | 52.68
0.119 | 4444.446 | 52.693
0.12 | 4611.113 | 53.689
0.121 | 4481.483 | 55.381
0.122 | 4555.557 | 55.67
0.123 | 4555.557 | 54.587
0.124 | 4351.853 | 52.946
0.125 | 4370.372 | 52.131
0.126 | 4388.89 | 51.473
0.127 | 4240.742 | 52.124
0.128 | 4444.446 | 53.028
0.129 | 4407.409 | 53.905
0.13 | 4314.816 | 53.459
0.131 | 4425.927 | 53.585
0.132 | 4277.779 | 54.201
0.133 | 4277.779 | 54.388
0.134 | 4425.927 | 52.841
0.135 | 4314.816 | 52.388
0.136 | 4462.964 | 54.323
0.137 | 4500.001 | 58.028
0.138 | 4351.853 | 58.61
0.139 | 4481.483 | 55.691
0.14 | 4425.927 | 54.026
0.141 | 4277.779 | 53.958
0.142 | 4425.927 | 53.225
0.143 | 4296.298 | 53.21
0.144 | 4314.816 | 53.107
0.145 | 4462.964 | 53.484
0.146 | 4277.779 | 53.973
0.147 | 4203.705 | 55.37
0.148 | 4314.816 | 55.59
0.149 | 4129.631 | 54.564
0.15 | 4277.779 | 54.863
0.151 | 4277.779 | 56.069
0.152 | 4203.705 | 55.723
0.153 | 4370.372 | 55.829
0.154 | 4351.853 | 56.982
0.155 | 4277.779 | 58.001
0.156 | 4425.927 | 57.51
0.157 | 4240.742 | 57.278
0.158 | 4240.742 | 57.668
0.159 | 4277.779 | 58.416
0.16 | 4148.15 | 58.52
0.161 | 4203.705 | 58.29
0.162 | 4296.298 | 57.408
0.163 | 4129.631 | 57.421
0.164 | 4203.705 | 58.886
0.165 | 4166.668 | 59.061
0.166 | 4055.557 | 58.708
0.167 | 4129.631 | 58.099
0.168 | 3981.483 | 55.592
0.17 | 4092.594 | 55.314
0.171 | 3981.483 | 57.928
0.172 | 4037.039 | 58.415
0.173 | 3962.964 | 55.605
0.175 | 3962.964 | 55.06
0.176 | 3870.372 | 57.728
0.178 | 4092.594 | 65.187
0.179 | 4129.631 | 64.84
0.18 | 4055.557 | 58.603
0.181 | 4129.631 | 57.449
0.182 | 4055.557 | 58.513
0.183 | 4092.594 | 60.467
0.184 | 4203.705 | 61.784
0.185 | 4055.557 | 63.066
0.186 | 4000.002 | 64.864
0.187 | 3722.224 | 65.583
0.188 | 3870.372 | 65.119
0.189 | 3888.89 | 62.302
0.19 | 3796.298 | 60.473
0.191 | 3870.372 | 60.523
0.192 | 3759.261 | 62.01
0.193 | 3685.187 | 63.467
0.194 | 3722.224 | 63.957
0.195 | 3592.594 | 62.686
0.196 | 3574.076 | 61.842
0.197 | 3611.113 | 63.867
0.198 | 3537.039 | 54.06
0.199 | 3629.631 | 44.617
0.2 | 3648.15 | 43.892
0.201 | 3500.002 | 45.064
0.202 | 3611.113 | 45.491
0.203 | 3537.039 | 45.378
0.204 | 3574.076 | 45.087
0.205 | 3648.15 | 45.079
0.206 | 3611.113 | 44.828
0.207 | 3925.928 | 44.859
0.209 | 4222.224 | 45.758
0.21 | 4314.816 | 46.29
0.211 | 4555.557 | 47.368
0.212 | 4759.261 | 48.34
0.213 | 4740.742 | 49.009
0.214 | 4962.964 | 49.62
0.215 | 4944.446 | 50.393
0.216 | 4888.89 | 51.281
0.218 | 5009.261 | 54.19
0.219 | 4944.446 | 57.367
0.221 | 5000.002 | 61.566
0.222 | 4944.446 | 62.321
0.223 | 4925.927 | 63.865
0.224 | 4722.224 | 67.714
0.225 | 4759.261 | 71.652
0.226 | 4722.224 | 73.5
0.227 | 4500.001 | 73.862
0.228 | 4537.038 | 73.146
0.229 | 4370.372 | 73.13
0.23 | 4166.668 | 73.757
0.231 | 4166.668 | 74.081
0.232 | 3861.113 | 74.076
0.233 | 3629.631 | 74.253
0.234 | 3333.335 | 74.624
0.235 | 3203.705 | 75.582
0.236 | 3129.631 | 77.422
0.237 | 2944.446 | 77.407
0.238 | 2935.187 | 74.784
0.239 | 2759.261 | 72.631
0.24 | 2759.261 | 72.469
0.241 | 2648.15 | 72.582
0.242 | 2611.113 | 72.227
0.243 | 2611.113 | 70.764
0.244 | 2462.965 | 67.875
0.245 | 2500.002 | 64.98
0.246 | 2574.076 | 62.504
0.247 | 2500.002 | 61.239
0.248 | 2611.113 | 60.849
0.249 | 2611.113 | 61.646
0.25 | 2574.076 | 62.371
0.251 | 2722.224 | 61.791
0.252 | 2796.298 | 60.937
0.254 | 2944.446 | 63.318
0.255 | 3166.668 | 64.476
0.256 | 3203.705 | 64.834
0.257 | 3296.298 | 65.592
0.258 | 3425.928 | 65.512
0.259 | 3314.817 | 64.773
0.26 | 3462.965 | 62.781
0.261 | 3537.039 | 59.629
0.262 | 3462.965 | 54.768
0.263 | 3574.076 | 51.217
0.264 | 3500.002 | 50.278
0.265 | 3388.891 | 50.185
0.266 | 3462.965 | 50.782
0.267 | 3351.854 | 51.269
0.268 | 3370.372 | 51.41
0.269 | 3537.039 | 50.821
0.27 | 3574.076 | 50.659
0.271 | 3833.335 | 51.588
0.273 | 4092.594 | 56.727
0.274 | 4055.557 | 56.404
0.275 | 4259.261 | 55.191
0.276 | 4314.816 | 53.482
0.277 | 4240.742 | 53.054
0.278 | 4444.446 | 52.497
0.279 | 4462.964 | 52.031
0.28 | 4462.964 | 51.686
0.281 | 4537.038 | 53.868
0.282 | 4333.335 | 57.446
0.283 | 4259.261 | 58.279
0.284 | 4333.335 | 57.742
0.285 | 4203.705 | 54.374
0.286 | 4333.335 | 52.359
0.287 | 4388.89 | 52.293
0.288 | 4314.816 | 53.594
0.289 | 4481.483 | 54.629
0.29 | 4444.446 | 54.996
0.291 | 4203.705 | 55.087
0.292 | 4277.779 | 55.114
0.293 | 4148.15 | 55.016
0.294 | 4111.113 | 54.093
0.295 | 4314.816 | 54.061
0.296 | 4277.779 | 54.516
0.297 | 4333.335 | 54.528
0.298 | 4407.409 | 50.398
0.299 | 4240.742 | 47.67
0.3 | 4314.816 | 46.831
0.301 | 4259.261 | 46.622
0.302 | 4166.668 | 46.847
0.303 | 4296.298 | 47.483
0.304 | 4314.816 | 47.934
0.305 | 4240.742 | 48.758
0.306 | 4351.853 | 50.96
0.307 | 4314.816 | 52.572
0.308 | 4407.409 | 53.932
0.309 | 4611.113 | 54.986
0.31 | 4537.038 | 55.228
0.311 | 4685.187 | 54.892
0.312 | 4814.816 | 56.171
0.313 | 4722.224 | 58.738
0.314 | 4870.372 | 60.396
0.315 | 4759.261 | 60.234
0.316 | 4574.075 | 59.046
0.317 | 4648.15 | 58.514
0.318 | 4500.001 | 59.056
0.319 | 4388.89 | 60.22
0.32 | 4500.001 | 61.66
0.321 | 4333.335 | 62.084
0.322 | 4277.779 | 61.25
0.323 | 4222.224 | 62.886
0.324 | 4000.002 | 64.726
0.325 | 4018.52 | 64.889
0.326 | 3925.928 | 63.406
0.328 | 3944.446 | 65.584
0.329 | 3759.261 | 65.411
0.33 | 3907.409 | 67.368
0.331 | 3740.742 | 68.949
0.332 | 3648.15 | 68.72
0.333 | 3648.15 | 67.059
0.334 | 3500.002 | 65.516
0.335 | 3500.002 | 65.252
0.336 | 3500.002 | 65.996
0.337 | 3388.891 | 67.534
0.338 | 3425.928 | 69.039
0.339 | 3351.854 | 70.951
0.34 | 3166.668 | 72.901
0.341 | 3240.742 | 71.848
0.342 | 3166.668 | 68.554
0.343 | 3203.705 | 68.484
0.344 | 3314.817 | 69.31
0.345 | 3222.224 | 69.924
0.346 | 3240.742 | 71.436
0.347 | 3203.705 | 73.811
0.348 | 3037.039 | 76.954
0.349 | 2944.446 | 81.099
0.35 | 2944.446 | 81.401
0.351 | 2907.409 | 74.741
0.352 | 3000.002 | 66.674
0.353 | 2944.446 | 67.12
0.354 | 2907.409 | 66.434
0.355 | 2861.113 | 66.838
0.356 | 2629.632 | 68.254
0.357 | 2388.891 | 71.135
0.358 | 2222.224 | 75.469
0.359 | 2444.446 | 81.056
0.36 | 2574.076 | 92.662
0.361 | 2648.15 | 111.077
0.362 | 2851.854 | 135.351
0.364 | 2870.372 | 117.276
0.365 | 2870.372 | 105.761
0.366 | 2666.669 | 100.043
0.367 | 2481.483 | 100.699
0.368 | 1384.262 | 105.599

## Test-7266
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7266
Scenario | 144 V - 17 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 143.7
Arc Current (A) | 7206
Arc Voltage (V) | 85.61
Duration of Arc (s) | 0.4925
Arc Energy (kJ) | 286.7
Incident Energy at 450 mm Distance (cal/cm²) | 1.36
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V) | I | Vbat
0.085 | 4550.696 | 68.254 | 0 | 144
0.09 | 7417.154 | 67.07 | 17000 | 0
0.095 | 8782.012 | 70.896
0.1 | 9024.226 | 72.374
0.105 | 8839.682 | 80.765
0.11 | 8385.344 | 79.847
0.115 | 8355.253 | 69.633
0.12 | 8851.216 | 68.501
0.125 | 9335.644 | 69.145
0.13 | 9220.304 | 74.528
0.135 | 8978.09 | 82.607
0.14 | 8109.194 | 94.996
0.145 | 6955.794 | 94.916
0.15 | 6440.608 | 85.911
0.155 | 7057.678 | 71.239
0.16 | 8355.253 | 67.964
0.165 | 9035.76 | 68.713
0.17 | 9347.178 | 67.527
0.175 | 9547.101 | 67.192
0.18 | 9474.052 | 66.477
0.185 | 9716.266 | 60.6
0.19 | 10339.103 | 56.954
0.195 | 10800.463 | 55.617
0.2 | 10950.405 | 57.432
0.205 | 10858.133 | 60.048
0.21 | 10846.599 | 62.261
0.215 | 10489.045 | 64.695
0.22 | 10246.831 | 65.742
0.225 | 10073.821 | 66.845
0.23 | 9670.13 | 67.06
0.235 | 9750.868 | 68.917
0.24 | 9623.994 | 72.817
0.245 | 9139.566 | 71.724
0.25 | 9170.323 | 62.804
0.255 | 9704.732 | 62.5
0.26 | 10085.355 | 62.452
0.265 | 10223.763 | 70.691
0.27 | 9408.693 | 74.873
0.275 | 9139.566 | 78.208
0.28 | 8401.389 | 79.698
0.285 | 8113.039 | 81.724
0.29 | 7986.165 | 82.577
0.295 | 7674.747 | 84.98
0.3 | 7421 | 88.81
0.305 | 7132.649 | 89.241
0.31 | 7005.774 | 91.251
0.315 | 6936.57 | 86.116
0.32 | 7051.911 | 86.885
0.325 | 7178.785 | 84.575
0.33 | 7271.057 | 78.855
0.335 | 7755.485 | 82.5
0.34 | 7594.009 | 78.667
0.345 | 7882.359 | 81.728
0.35 | 7893.893 | 85.65
0.355 | 7363.329 | 86.282
0.36 | 7109.58 | 93.424
0.365 | 6648.22 | 93.321
0.37 | 6325.268 | 91.479
0.375 | 6452.142 | 86.044
0.38 | 6809.696 | 84.469
0.385 | 7051.911 | 86.917
0.39 | 6901.968 | 95.798
0.395 | 6181.093 | 117.306
0.4 | 5010.391 | 96.977
0.405 | 5437.149 | 100.05
0.41 | 5333.343 | 107.842
0.415 | 4025.277 | 144.226
0.42 | 2392.171 | 100.741
0.425 | 4030 | 88.204
0.43 | 5575.557 | 86.983
0.435 | 6509.812 | 81.52
0.44 | 7144.183 | 81.423
0.445 | 7444.067 | 84.044
0.45 | 7524.805 | 84.181
0.455 | 7386.397 | 76.74
0.46 | 7916.961 | 78.107
0.465 | 7974.631 | 86.645
0.47 | 7236.455 | 108.555
0.475 | 5079.595 | 117.547
0.48 | 3430.232 | 95.905
0.485 | 5125.731 | 86.323
0.49 | 6225.307 | 91.11
0.495 | 6232.996 | 100.853
0.5 | 5448.683 | 123.368
0.505 | 4848.915 | 101.639
0.51 | 5033.459 | 99.973
0.515 | 5148.799 | 105.688
0.52 | 4722.041 | 92.567
0.525 | 5794.703 | 84.68
0.53 | 6555.948 | 90.297
0.535 | 6394.472 | 104.626
0.54 | 5471.751 | 113.552
0.545 | 4249.146 | 115.498
0.55 | 4006.932 | 104.131
0.555 | 4187.632 | 123.477
0.56 | 1892.913 | 142.904
0.565 | 881.216 | 121.035
0.57 | 650.536 | 155.119

## Test-7267
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7267
Scenario | 144 V - 17 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 143.5
Arc Current (A) | 7788
Arc Voltage (V) | 80.68
Duration of Arc (s) | 0.483
Arc Energy (kJ) | 293.3
Incident Energy at 450 mm Distance (cal/cm²) | 1.65
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline |  | I | Vbat
|  |  | 0 | 144
Time (s) | Current (A) | Voltage (V) | 17000 | 0
0.087 | 9001.173 | 62.664
0.092 | 9527.685 | 62.306
0.097 | 9642.144 | 65.347
0.102 | 9802.387 | 65.936
0.107 | 9619.252 | 67.607
0.112 | 9436.118 | 69.097
0.117 | 8886.714 | 68.953
0.121 | 8154.176 | 75.938
0.126 | 8486.108 | 81.294
0.127 | 8886.714 | 80.703
0.132 | 9756.603 | 74.776
0.133 | 10168.655 | 71.17
0.137 | 9985.521 | 59.33
0.142 | 10099.98 | 60.956
0.148 | 10214.439 | 63.938
0.153 | 10191.547 | 61.489
0.158 | 10306.006 | 61.222
0.162 | 10099.98 | 60.827
0.163 | 10489.141 | 60.574
0.168 | 10626.492 | 63.098
0.173 | 11027.099 | 57.669
0.178 | 11084.328 | 55.929
0.183 | 10901.193 | 54.444
0.188 | 10443.357 | 58.72
0.193 | 10306.006 | 62.94
0.198 | 10397.574 | 62.801
0.202 | 10077.088 | 61.183
0.207 | 9939.737 | 64.406
0.208 | 10168.655 | 63.51
0.212 | 9779.495 | 64.098
0.217 | 9756.603 | 63.007
0.222 | 9596.36 | 66.426
0.227 | 9596.36 | 69.853
0.232 | 9436.118 | 66.633
0.237 | 9161.416 | 70.741
0.241 | 8680.688 | 70.613
0.246 | 8291.527 | 77.786
0.251 | 8039.717 | 77.211
0.256 | 8016.826 | 82.318
0.261 | 7833.691 | 77.189
0.266 | 7810.799 | 81.199
0.271 | 7604.773 | 80.584
0.276 | 7627.665 | 81.796
0.281 | 7787.908 | 82.805
0.286 | 7627.665 | 81.543
0.29 | 7284.288 | 80.921
0.295 | 7307.18 | 87.13
0.3 | 7352.963 | 83.69
0.305 | 7192.721 | 87.198
0.31 | 6620.425 | 84.754
0.315 | 6368.616 | 93.615
0.319 | 5887.888 | 93.802
0.325 | 6952.357 | 101.074
0.331 | 8039.717 | 74.771
0.336 | 8085.501 | 74.046
0.341 | 8245.744 | 79.08
0.346 | 8314.419 | 76.84
0.351 | 8245.744 | 75.303
0.356 | 7833.691 | 78.323
0.361 | 8154.176 | 83.02
0.366 | 8337.311 | 75.334
0.371 | 8154.176 | 76.447
0.376 | 7993.934 | 78.035
0.381 | 8131.285 | 83.637
0.386 | 7696.34 | 77.94
0.39 | 7330.071 | 83.682
0.395 | 6746.331 | 83.87
0.399 | 6231.265 | 92.093
0.405 | 6826.452 | 98.942
0.41 | 6322.832 | 84.929
0.415 | 6345.724 | 96.041
0.42 | 6368.616 | 91.34
0.425 | 6986.694 | 91.463
0.43 | 6803.56 | 84.204
0.435 | 6666.209 | 88.221
0.44 | 6483.075 | 91.695
0.445 | 6803.56 | 91.861
0.45 | 7398.747 | 84.968
0.456 | 7696.34 | 80.482
0.46 | 6918.019 | 77.743
0.464 | 6116.806 | 87.339
0.47 | 6826.452 | 106.074
0.475 | 6929.465 | 81.43
0.48 | 6437.291 | 87.662
0.484 | 5773.429 | 93.36
0.489 | 5521.619 | 103.362
0.494 | 6071.022 | 98.216
0.5 | 7169.829 | 90.09
0.505 | 7513.206 | 79.745
0.51 | 7398.747 | 80.186
0.515 | 6734.884 | 84.497
0.519 | 6025.238 | 89.74
0.524 | 5567.402 | 102.815
0.528 | 4903.54 | 101.185
0.534 | 5338.484 | 106.778
0.539 | 5155.35 | 97.185
0.543 | 3907.746 | 102.179
0.548 | 4148.11 | 134.872
0.552 | 2957.737 | 104.328
0.555 | 691.447 | 116.659
0.556 | 1195.067 | 122.486

## Test-7268
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7268
Scenario | 144 V - 17 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 143.5
Arc Current (A) | 8004
Arc Voltage (V) | 78.72
Duration of Arc (s) | 0.4539
Arc Energy (kJ) | 275.6
Incident Energy at 450 mm Distance (cal/cm²) | 1.17
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 144
0.085 | 4522.501 | 65.577 | 17000 | 0
0.09 | 7335.138 | 62.866
0.095 | 8798.624 | 63.553
0.1 | 9507.5 | 65.336
0.105 | 9713.303 | 68.389
0.11 | 9621.835 | 66.067
0.115 | 9713.303 | 65.588
0.12 | 9713.303 | 65.024
0.125 | 9804.771 | 66.634
0.13 | 9621.835 | 64.976
0.135 | 9850.505 | 64.602
0.14 | 9919.106 | 64.83
0.145 | 9873.372 | 64.343
0.15 | 9873.372 | 59.262
0.155 | 10102.042 | 59.285
0.16 | 10536.514 | 51.82
0.165 | 10948.119 | 52.214
0.17 | 11245.39 | 55.547
0.175 | 11222.523 | 58.579
0.18 | 10925.252 | 62.187
0.185 | 10765.184 | 63.543
0.19 | 10399.312 | 59.143
0.195 | 10399.312 | 62.547
0.2 | 10490.78 | 68.291
0.205 | 9941.973 | 72.197
0.21 | 9507.5 | 70.511
0.215 | 9164.496 | 70.601
0.22 | 8935.826 | 67.846
0.225 | 9095.895 | 68.595
0.23 | 9141.629 | 69.619
0.235 | 9324.565 | 69.833
0.24 | 9164.496 | 68.994
0.245 | 9278.831 | 71.38
0.25 | 9233.097 | 74.477
0.255 | 8935.826 | 76.723
0.26 | 8661.422 | 72.5
0.265 | 8730.023 | 72.954
0.27 | 8730.023 | 71.598
0.275 | 8821.491 | 77.864
0.28 | 8409.886 | 76.855
0.285 | 8524.221 | 78.324
0.29 | 8409.886 | 82.124
0.295 | 7723.877 | 67.913
0.3 | 8478.487 | 66.469
0.305 | 9027.294 | 70.353
0.31 | 9301.698 | 72.354
0.315 | 9141.629 | 79.868
0.32 | 8478.487 | 82.817
0.325 | 8135.482 | 87.158
0.33 | 7380.872 | 83.359
0.335 | 7380.872 | 87.134
0.34 | 7266.537 | 88.552
0.345 | 7015.001 | 87.2
0.35 | 6923.533 | 81.045
0.355 | 7129.335 | 85.94
0.36 | 7197.936 | 87.794
0.365 | 6923.533 | 79.04
0.37 | 7403.739 | 77.791
0.375 | 7883.945 | 78.497
0.38 | 7838.212 | 74.074
0.385 | 8158.349 | 77.968
0.39 | 8226.95 | 78.535
0.395 | 8181.216 | 76.482
0.4 | 8272.684 | 76.589
0.405 | 8226.95 | 79.758
0.41 | 8044.014 | 81.424
0.415 | 7861.079 | 82.473
0.42 | 7723.877 | 86.79
0.425 | 7540.941 | 89.255
0.43 | 6969.267 | 89.858
0.435 | 6649.129 | 91.768
0.44 | 6671.996 | 93.18
0.445 | 6397.592 | 101.063
0.45 | 5803.051 | 101.838
0.455 | 5345.712 | 94.648
0.46 | 5642.982 | 96.25
0.465 | 5642.982 | 100.666
0.47 | 5482.914 | 99.749
0.475 | 5391.446 | 98.169
0.48 | 5277.111 | 97.958
0.485 | 5460.047 | 88.511
0.49 | 5985.987 | 83.779
0.495 | 6740.597 | 88.486
0.5 | 6900.666 | 93.114
0.505 | 6580.528 | 101.058
0.51 | 5757.317 | 102.122
0.515 | 5460.047 | 107.039
0.52 | 5002.707 | 148.033
0.525 | 2327.272 | 166.091
0.53 | 1549.795 | 150.845

## Test-7269
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7269
Scenario | 144 V - 17 kA Available - 6mm gap, ceramic box, cotton T-shift/mannequin test
Test Voltage (V) | 143.6
Arc Current (A) | 6418
Arc Voltage (V) | 91.46
Duration of Arc (s) | 0.7736
Arc Energy (kJ) | 406.9
Incident Energy at 450 mm Distance (cal/cm²) | 0.01 (t-shirt)
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V)
0.08 | 117.008 | 8.617
0.085 | 2576.559 | 55.989
0.09 | 6460.579 | 60.158
0.095 | 8567.773 | 63.947
0.1 | 9327.244 | 63.568
0.105 | 9608.729 | 66.979
0.11 | 9668.142 | 68.874
0.115 | 9532.834 | 71.527
0.12 | 9345.936 | 66.79
0.125 | 9302.597 | 68.874
0.13 | 9512.779 | 65.084
0.135 | 9732.716 | 63 | I | Vbat
0.14 | 9891.154 | 64.137 | 0 | 144
0.145 | 10073.3 | 71.148 | 17000 | 0
0.15 | 9806.094 | 63.758
0.155 | 9723.942 | 53.715
0.16 | 10495.528 | 48.788
0.165 | 11078.368 | 49.546
0.17 | 11549.615 | 52.578
0.175 | 11516.744 | 60.347
0.18 | 11030.534 | 62.432
0.185 | 10513.643 | 64.326
0.19 | 10198.232 | 67.737
0.195 | 9819.233 | 70.39
0.2 | 9565.459 | 68.874
0.205 | 9501.821 | 69.253
0.21 | 9361.741 | 57.884
0.215 | 9648.623 | 55.989
0.22 | 10392.696 | 59.021
0.225 | 10552.814 | 59.4
0.23 | 10602.473 | 63
0.235 | 10401.103 | 61.673
0.24 | 10354.945 | 62.432
0.245 | 10254.792 | 63.947
0.25 | 10076.74 | 71.906
0.255 | 9633.051 | 74.559
0.26 | 9136.389 | 70.011
0.265 | 9083.864 | 72.664
0.27 | 8955.329 | 72.664
0.275 | 8691.794 | 73.801
0.28 | 8627.279 | 74.938
0.285 | 8656.072 | 77.97
0.29 | 8588.93 | 71.906
0.295 | 8681.354 | 66.6
0.3 | 8945.431 | 70.011
0.305 | 9128.32 | 68.874
0.31 | 9066.603 | 73.422
0.315 | 8914.63 | 76.454
0.32 | 8604.407 | 81.759
0.325 | 8189.781 | 87.065
0.33 | 7567.325 | 90.097
0.335 | 7188.298 | 78.348
0.34 | 7369.549 | 84.412
0.345 | 7516.551 | 80.433
0.35 | 7547.729 | 84.791
0.355 | 7399.969 | 86.307
0.36 | 7220.39 | 86.686
0.365 | 7118.86 | 90.287
0.37 | 6824.597 | 77.97
0.375 | 7180.09 | 75.696
0.38 | 7654.471 | 77.212
0.385 | 7828.704 | 79.485
0.39 | 7902.123 | 82.707
0.395 | 7629.154 | 91.613
0.4 | 7156.86 | 80.243
0.405 | 7407.909 | 77.969
0.41 | 7762.45 | 86.497
0.415 | 7387.932 | 96.918
0.42 | 6602.283 | 80.622
0.425 | 6811.195 | 98.813
0.43 | 6117.258 | 96.919
0.435 | 5912.297 | 83.654
0.44 | 6480.153 | 84.033
0.445 | 7034.543 | 87.065
0.45 | 7086.753 | 82.896
0.455 | 7053.062 | 88.771
0.46 | 7186.038 | 72.285
0.465 | 7697.58 | 74.559
0.47 | 8170.69 | 80.243
0.475 | 8044.13 | 81.949
0.48 | 7692.997 | 90.097
0.485 | 7259.37 | 91.234
0.49 | 6832.874 | 90.855
0.495 | 6607.667 | 97.171
0.5 | 6052.59 | 98.055
0.505 | 5777.288 | 98.434
0.51 | 5572.821 | 96.918
0.515 | 5419.986 | 98.624
0.52 | 5515.262 | 101.213
0.525 | 5397.434 | 100.898
0.53 | 5023.851 | 106.204
0.535 | 4624.99 | 103.74
0.54 | 4643.863 | 105.067
0.545 | 4570.832 | 98.055
0.55 | 4751.509 | 94.265
0.555 | 5308.364 | 88.202
0.56 | 6053.899 | 88.96
0.565 | 6226.901 | 104.119
0.57 | 5507.394 | 97.108
0.575 | 5474.546 | 95.024
0.58 | 6109.564 | 79.485
0.585 | 6861.641 | 84.791
0.59 | 6999.338 | 91.613
0.595 | 6712.386 | 108.667
0.6 | 5217.472 | 88.581
0.605 | 5507.514 | 91.992
0.61 | 5977.62 | 88.328
0.615 | 6356.29 | 87.444
0.62 | 6731.545 | 91.044
0.625 | 6460.336 | 109.425
0.63 | 4849.008 | 108.667
0.64 | 2409.851 | 123.068
0.645 | 1218.118 | 152.06
0.65 | 825.912 | 157.555
0.655 | 367.867 | 128.898
0.66 | 1139.376 | 127.84
0.665 | 1873.084 | 124.963
0.675 | 1059.057 | 126.352
0.68 | 1295.357 | 124.205
0.685 | 1226.807 | 118.773
0.69 | 1710.882 | 115.867
0.695 | 2871.393 | 95.592
0.7 | 4389.797 | 97.676
0.705 | 4922.038 | 113.214
0.71 | 4329.4 | 106.014
0.715 | 4455.387 | 106.014
0.72 | 4705.328 | 98.434
0.725 | 5122.348 | 97.676
0.73 | 5485.452 | 92.371
0.735 | 5807.285 | 103.361
0.74 | 5489.404 | 94.139
0.745 | 5702.121 | 106.772
0.75 | 4903.983 | 113.214
0.755 | 3762.56 | 117.762
0.76 | 2877.231 | 141.638
0.765 | 1894.985 | 123.826
0.77 | 1999.793 | 98.75
0.775 | 3953.39 | 80.433
0.78 | 5715.428 | 99.192
0.785 | 5626.299 | 98.434
0.79 | 5247.269 | 111.698
0.795 | 4120.046 | 136.143
0.8 | 2985.818 | 97.297
0.805 | 4200.813 | 97.297
0.81 | 4892.12 | 99.95
0.815 | 4991.407 | 108.667
0.82 | 4349.318 | 159.601
0.825 | 791.47 | 154.713
0.84 | 142.756 | 101.336
0.845 | 2014.113 | 134.058
0.85 | 601.841 | 153.765
0.855 | 114.642 | 135.953
0.87 | 115.149 | 135.195

## Test-7270
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7270
Scenario | 144 V - 17 kA Available - 6mm gap, open air, calorimeters at 18"
Test Voltage (V) | 143.4
Arc Current (A) | 7810
Arc Voltage (V) | 80.06
Duration of Arc (s) | 0.4002
Arc Energy (kJ) | 243.3
Incident Energy at 450 mm Distance (cal/cm²) | 0.74
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V) | I | Vbat
0.085 | 5386.639 | 59.431 | 0 | 144
0.09 | 8169.448 | 63.241 | 17000 | 0
0.095 | 9099.762 | 63.622
0.1 | 9526.694 | 65.907
0.105 | 9629.575 | 68.955
0.11 | 9537.59 | 66.288
0.115 | 9665.548 | 64.002
0.12 | 9822.5 | 64.002
0.125 | 9948.139 | 65.145
0.13 | 9983.069 | 65.145
0.135 | 10130.522 | 62.479
0.14 | 10130.568 | 64.002
0.145 | 10215.723 | 56.764
0.15 | 10797.692 | 54.098
0.155 | 11205.261 | 52.574
0.16 | 10955.189 | 58.669
0.165 | 10710.572 | 60.955
0.17 | 10178.675 | 65.907
0.175 | 9727.904 | 68.955
0.18 | 9421.817 | 68.574
0.185 | 9268.868 | 69.717
0.19 | 9034.048 | 76.955
0.195 | 8933.81 | 70.479
0.2 | 9170.976 | 70.098
0.205 | 9298.664 | 69.717
0.21 | 9196.204 | 69.717
0.215 | 8917.533 | 75.812
0.22 | 8899.544 | 72.002
0.225 | 8800.041 | 80.383
0.23 | 9592.508 | 57.526
0.235 | 9866.44 | 64.002
0.24 | 9362.001 | 77.716
0.245 | 8511.861 | 80.383
0.25 | 8068.588 | 78.478
0.255 | 7809.171 | 83.812
0.26 | 7394.607 | 86.478
0.265 | 6945.361 | 92.954
0.27 | 7110.037 | 74.288
0.275 | 7544.632 | 80.002
0.28 | 7685.348 | 81.526
0.285 | 7478.595 | 86.859
0.29 | 7344.173 | 86.097
0.295 | 7065.174 | 89.145
0.3 | 7273.999 | 82.669
0.305 | 8017.226 | 70.859
0.31 | 8639.863 | 70.098
0.315 | 8629.094 | 76.193
0.32 | 8177.602 | 80.764
0.325 | 8062.465 | 80.002
0.33 | 7944.832 | 79.24
0.335 | 7453.096 | 93.716
0.34 | 7343.839 | 87.24
0.345 | 6539.327 | 97.907
0.35 | 6033.526 | 93.335
0.355 | 5787.921 | 94.097
0.36 | 5234.441 | 106.287
0.365 | 5467.748 | 96.383
0.37 | 5700.869 | 95.24
0.375 | 6050.114 | 89.907
0.38 | 6489.207 | 86.859
0.385 | 6910.218 | 83.812
0.39 | 7399.285 | 80.764
0.395 | 7629.594 | 79.24
0.4 | 7591.376 | 88.002
0.405 | 7793.375 | 79.24
0.41 | 7848.859 | 79.621
0.415 | 7745.224 | 81.907
0.42 | 7340.296 | 89.145
0.425 | 7188.716 | 85.716
0.43 | 6941.444 | 89.907
0.435 | 6918.21 | 84.574
0.44 | 7082.432 | 85.335
0.445 | 6809.157 | 91.431
0.45 | 6081.378 | 93.335
0.455 | 5774.518 | 100.573
0.46 | 4614.52 | 116.573
0.465 | 4752.934 | 102.097
0.47 | 4754.427 | 103.621
0.475 | 2858.903 | 135.62

## Test-7271
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7271
Scenario | 144 V - 17 kA available - 6mm gap, open air, calorimeters at 18"
Test Voltage (V) | 143.4
Arc Current (A) | 7178
Arc Voltage (V) | 84.91
Duration of Arc (s) | 0.4624
Arc Energy (kJ) | 259.6
Incident Energy at 450 mm Distance (cal/cm²) | 0.77
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 144
0.085 | 6390.331 | 63.863 | 17000 | 0
0.09 | 8392.122 | 63.231
0.095 | 9160.251 | 65.23
0.1 | 9346.464 | 67.554
0.105 | 9649.06 | 66.855
0.11 | 9532.677 | 66.621
0.115 | 9835.273 | 63.538
0.12 | 9951.656 | 63.913
0.125 | 9998.209 | 62.046
0.13 | 10300.806 | 62.501
0.135 | 10533.572 | 58.254
0.14 | 10952.551 | 54.448
0.145 | 10859.445 | 56.336
0.15 | 10743.062 | 58.721
0.155 | 10673.232 | 61.081
0.16 | 10091.316 | 65.331
0.165 | 9695.613 | 66.748
0.17 | 9323.187 | 70.62
0.175 | 8717.995 | 74.257
0.18 | 8368.845 | 79.281
0.185 | 8415.398 | 75.32
0.19 | 8112.802 | 78.516
0.195 | 7554.163 | 84.306
0.2 | 7693.823 | 80.761
0.205 | 8671.441 | 70.072
0.21 | 9765.443 | 58.007
0.215 | 10580.125 | 55.527
0.22 | 10696.508 | 56.515
0.225 | 10440.465 | 60.25
0.23 | 9881.826 | 68.953
0.235 | 9416.294 | 71.104
0.24 | 8904.208 | 72.694
0.245 | 8578.335 | 75.067
0.25 | 8485.228 | 76.18
0.255 | 8019.696 | 82.358
0.26 | 7554.163 | 87.264
0.265 | 7274.843 | 87.558
0.27 | 7414.503 | 81.236
0.275 | 6809.311 | 91.757
0.28 | 7530.886 | 77.359
0.285 | 8136.079 | 74.847
0.29 | 8415.398 | 73.585
0.295 | 8345.568 | 76.347
0.3 | 8415.398 | 74.978
0.305 | 8182.632 | 79.816
0.31 | 8205.909 | 75.212
0.315 | 8322.292 | 76.797
0.32 | 8438.675 | 72.15
0.325 | 8531.781 | 72.371
0.33 | 7717.099 | 87.595
0.335 | 6995.524 | 85.875
0.34 | 6297.225 | 96.529
0.345 | 6227.395 | 93.824
0.35 | 6204.118 | 91.194
0.355 | 5854.969 | 100.286
0.36 | 4993.733 | 108.621
0.365 | 4854.073 | 104.753
0.37 | 4737.69 | 106.943
0.375 | 5203.223 | 96.176
0.38 | 6064.458 | 87.698
0.385 | 6716.204 | 85.676
0.39 | 7321.396 | 81.335
0.395 | 7973.142 | 72.931
0.4 | 7973.142 | 78.399
0.405 | 7973.142 | 80.354
0.41 | 7740.376 | 80.853
0.415 | 8252.462 | 74.445
0.42 | 8578.335 | 71.472
0.425 | 8555.058 | 72.967
0.43 | 8694.718 | 74.228
0.435 | 8159.355 | 81.16
0.44 | 7344.673 | 88.483
0.445 | 7391.226 | 83.04
0.45 | 7042.077 | 86.5
0.455 | 5831.692 | 101.285
0.46 | 5110.116 | 107.297
0.465 | 4923.903 | 104.534
0.47 | 4295.434 | 111.869
0.475 | 2782.453 | 129.674
0.48 | 1525.515 | 131.143
0.485 | 1688.451 | 129.27
0.49 | 1595.344 | 130.318
0.495 | 2968.666 | 95.038
0.5 | 2666.07 | 121.198
0.505 | 3736.795 | 104.528
0.51 | 4365.264 | 102.892
0.515 | 4667.86 | 103.351
0.52 | 3341.092 | 129.221
0.525 | 1176.365 | 143.416
0.53 | 780.662 | 142.701

## Test-7272
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7272
Scenario | 144 V - 17 kA available - 6mm gap, open air, calorimeters at 18"
Test Voltage (V) | 143.6
Arc Current (A) | 7227
Arc Voltage (V) | 83.83
Duration of Arc (s) | 0.2725
Arc Energy (kJ) | 153.8
Incident Energy at 450 mm Distance (cal/cm²) | 0.47
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 144
0.085 | 2327.228 | 64.565 | 17000 | 0
0.09 | 5867.202 | 70.208
0.095 | 7634.887 | 71.336
0.1 | 8295.61 | 75.099
0.105 | 8385.928 | 81.87
0.11 | 8023.304 | 85.632
0.115 | 7350.004 | 98.047
0.12 | 6022.384 | 144.886
0.125 | 1926.053 | 144.07
0.13 | 2056.496 | 113.472
0.135 | 3026.603 | 105.571
0.14 | 4206.228 | 70.96
0.145 | 6662.792 | 65.693
0.15 | 8233.313 | 69.079
0.155 | 8952.717 | 66.822
0.16 | 9330.92 | 64.188
0.165 | 9488.775 | 69.079
0.17 | 9534.548 | 60.426
0.175 | 9927.305 | 57.417
0.18 | 10346.478 | 54.031
0.185 | 10819.318 | 52.526
0.19 | 11163.351 | 61.931
0.195 | 10955.919 | 70.96
0.2 | 9916.646 | 74.722
0.205 | 9034.294 | 83.375
0.21 | 8198.393 | 78.108
0.215 | 7912.354 | 87.89
0.22 | 7459.191 | 95.038
0.225 | 6827.047 | 95.038
0.23 | 6337.256 | 70.96
0.235 | 7618.855 | 64.941
0.24 | 8819.222 | 72.089
0.245 | 9085.085 | 70.96
0.25 | 9047.071 | 74.722
0.255 | 8796.822 | 83.751
0.26 | 8179.497 | 80.929
0.265 | 7765.579 | 70.584
0.27 | 8228.13 | 74.346
0.275 | 8480.46 | 70.96
0.28 | 8683.418 | 64.941
0.285 | 9227.586 | 70.02
0.29 | 9235.244 | 67.574
0.295 | 9467.54 | 75.099
0.3 | 8975.89 | 84.504
0.305 | 8045.328 | 117.046
0.31 | 6326.623 | 84.504
0.315 | 6732.091 | 86.385
0.32 | 7096.378 | 84.128
0.325 | 7217.808 | 96.919
0.33 | 6414.566 | 104.255
0.335 | 5065.833 | 148.46
0.345 | 1147.188 | 152.598
0.35 | 484.931 | 160.874

## Test-7273
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7273
Scenario | 144 V - 17 kA Available - 25mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 143.5
Arc Current (A) | 888.2
Arc Voltage (V) | 124.2
Duration of Arc (s) | 0.02082
Arc Energy (kJ) | 2.435
Incident Energy at 450 mm Distance (cal/cm²) | 0.02
Electrode Gap (mm) | 25
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 144
0.081 | 1151.116 | 33.78 | 17000 | 0
0.082 | 2054.711 | 103.685
0.083 | 2423.055 | 103.048
0.084 | 2515.141 | 125.817
0.085 | 2192.84 | 149.701
0.086 | 1732.41 | 160.001
0.087 | 949.678 | 155.855
0.088 | 1133.85 | 112.63
0.089 | 1410.108 | 137.001
0.09 | 949.678 | 159.355
0.091 | 673.42 | 151.441
0.092 | 443.205 | 141.278
0.093 | 443.205 | 145.165
0.094 | 351.119 | 143.115
0.095 | 443.205 | 129.787
0.096 | 581.334 | 146.192
0.097 | 443.205 | 143.886
0.098 | 305.076 | 142.897
0.099 | 351.119 | 148.105

## Test-7274
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7274
Scenario | 144 V - 17 kA Available - 25mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 143.9
Arc Current (A) | 5121
Arc Voltage (V) | 99.81
Duration of Arc (s) | 0.05043
Arc Energy (kJ) | 24.67
Incident Energy at 450 mm Distance (cal/cm²) | 0.07
Electrode Gap (mm) | 25
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 144
0.085 | 1478.444 | 65.4 | 17000 | 0
0.086 | 2665.561 | 67.694
0.087 | 3621.046 | 69.988
0.088 | 4286.99 | 70.562
0.089 | 4866.071 | 70.562
0.09 | 5647.831 | 71.136
0.091 | 6140.051 | 72.283
0.092 | 6400.638 | 75.151
0.093 | 6863.903 | 78.019
0.094 | 7356.122 | 79.166
0.095 | 7471.939 | 80.313
0.096 | 7558.801 | 78.019
0.097 | 7819.388 | 77.445
0.098 | 7761.479 | 78.592
0.099 | 7761.479 | 82.607
0.1 | 7906.25 | 87.196
0.101 | 7848.342 | 90.064
0.102 | 7935.204 | 91.785
0.103 | 8051.02 | 96.374
0.104 | 7790.434 | 98.095
0.105 | 7732.525 | 99.242
0.106 | 7500.893 | 99.242
0.107 | 7240.306 | 99.242
0.108 | 7066.582 | 103.83
0.109 | 6748.087 | 108.993
0.11 | 6661.224 | 112.434
0.111 | 6429.592 | 119.318
0.112 | 6169.005 | 126.201
0.113 | 5908.418 | 108.419
0.114 | 5618.877 | 90.064
0.115 | 5184.566 | 89.491
0.116 | 4808.163 | 101.536
0.117 | 4489.668 | 110.14
0.118 | 4779.209 | 113.582
0.119 | 5097.704 | 118.17
0.121 | 5039.796 | 122.759
0.122 | 4721.301 | 125.627
0.123 | 4576.53 | 131.937
0.127 | 3360.459 | 151.439
0.128 | 2926.148 | 178.971
0.129 | 2578.699 | 173.809
0.13 | 2260.204 | 145.703

## Test-7275
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7275
Scenario | 274 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 273.7
Arc Current (A) | 10880
Arc Voltage (V) | 114.1
Duration of Arc (s) | 0.7543
Arc Energy (kJ) | 885.2
Incident Energy at 450 mm Distance (cal/cm²) | 6.01
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V) | I | Vbat
0.08 | 12758.792 | 2.319 | 0 | 274
0.085 | 14001.733 | 65.648 | 20000 | 0
0.09 | 14217.045 | 68.437
0.095 | 14190.947 | 71.161
0.1 | 14021.307 | 75.863
0.105 | 14334.488 | 73.599
0.11 | 14334.488 | 73.333
0.115 | 14595.473 | 71.872
0.12 | 14673.769 | 68.709
0.125 | 14765.114 | 65.974
0.13 | 14843.409 | 61.189
0.135 | 14725.966 | 59.549
0.14 | 14647.67 | 64.366
0.145 | 14438.883 | 67.721
0.15 | 14047.405 | 67.978
0.155 | 14373.636 | 71.715
0.16 | 14569.375 | 71.664
0.165 | 14471.506 | 68.127
0.17 | 13969.11 | 65.596
0.175 | 13747.272 | 75.106
0.18 | 14177.898 | 78.059
0.185 | 13786.42 | 74.532
0.19 | 13747.272 | 76.067
0.195 | 13655.894 | 78.845
0.2 | 13251.401 | 78.893
0.205 | 13394.943 | 78.01
0.21 | 12925.17 | 85.582
0.215 | 12416.249 | 89.987
0.22 | 13081.761 | 96.247
0.225 | 13329.696 | 91.876
0.23 | 13342.746 | 79.016
0.235 | 12820.776 | 82.077
0.24 | 13081.761 | 85.108
0.245 | 12977.367 | 88.031
0.25 | 12964.318 | 84.627
0.255 | 12807.727 | 85.784
0.26 | 12494.545 | 88.578
0.265 | 12103.067 | 93.813
0.27 | 11966.05 | 96.856
0.275 | 11763.121 | 103.15
0.28 | 12337.954 | 104.495
0.285 | 12403.2 | 98.537
0.29 | 11966.05 | 90.083
0.295 | 12181.363 | 93.44
0.3 | 12546.742 | 99.175
0.305 | 12872.973 | 91.232
0.31 | 12533.693 | 89.018
0.315 | 12559.791 | 89.316
0.32 | 12435.823 | 92.706
0.325 | 12416.249 | 92.523
0.33 | 12514.119 | 92.33
0.335 | 12181.363 | 94.283
0.34 | 11946.477 | 95.27
0.345 | 11711.59 | 100.626
0.35 | 11163.522 | 104.554
0.355 | 10948.209 | 112.064
0.36 | 10243.55 | 119.55
0.365 | 10223.976 | 124.966
0.37 | 10635.027 | 129.164
0.375 | 11437.556 | 115.096
0.38 | 11594.147 | 107.403
0.385 | 11359.26 | 107.378
0.39 | 11104.8 | 106.544
0.395 | 11183.096 | 110.538
0.4 | 11463.655 | 109.791
0.405 | 11711.59 | 106.971
0.41 | 11450.605 | 105.383
0.415 | 11359.26 | 105.489
0.42 | 11183.096 | 110.974
0.425 | 11633.295 | 108.347
0.43 | 11966.05 | 101.84
0.435 | 11280.965 | 98.935
0.44 | 10869.914 | 108.668
0.445 | 10693.749 | 115.137
0.45 | 11202.67 | 120.766
0.455 | 11241.817 | 107.802
0.46 | 10993.882 | 111.458
0.465 | 10928.635 | 117.968
0.47 | 10635.027 | 113.983
0.475 | 10869.914 | 124.589
0.48 | 10458.863 | 112.714
0.485 | 10419.715 | 123.599
0.49 | 10693.749 | 118.968
0.495 | 10615.453 | 114.489
0.5 | 10210.927 | 124.889
0.505 | 10458.863 | 130.366
0.51 | 10328.37 | 120.058
0.515 | 10713.323 | 122.061
0.52 | 10869.914 | 116.71
0.525 | 10732.897 | 112.268
0.53 | 10615.453 | 117.579
0.535 | 10067.385 | 118.48
0.54 | 9852.073 | 125.829
0.545 | 9871.647 | 135.381
0.55 | 9852.073 | 129.922
0.555 | 9362.726 | 122.805
0.56 | 8853.805 | 141.232
0.565 | 9362.726 | 143.205
0.57 | 8971.249 | 136.421
0.575 | 8599.345 | 142.101
0.58 | 8853.805 | 152.693
0.585 | 8501.476 | 150.663
0.59 | 8814.658 | 145.325
0.595 | 8658.067 | 139.736
0.6 | 8697.214 | 146.64
0.605 | 8442.754 | 150.534
0.61 | 7757.669 | 146.667
0.615 | 8971.249 | 170.289
0.62 | 8912.527 | 133.214
0.625 | 9147.413 | 136.822
0.63 | 10106.533 | 139.573
0.635 | 9695.482 | 119.368
0.64 | 9147.413 | 127.98
0.645 | 8658.067 | 142.35
0.65 | 8814.658 | 151.774
0.655 | 9166.987 | 145.011
0.66 | 8834.231 | 135.714
0.665 | 8697.214 | 141.048
0.67 | 7875.112 | 148.459
0.675 | 8305.737 | 159.584
0.68 | 8364.459 | 150.867
0.685 | 8051.277 | 145.583
0.69 | 5828.816 | 151.395
0.695 | 9304.004 | 171.787
0.7 | 9675.908 | 120.16
0.705 | 9649.809 | 129.854
0.71 | 9949.942 | 135.211
0.715 | 9832.499 | 124.121
0.72 | 9695.482 | 128.617
0.725 | 9597.612 | 133.909
0.73 | 9392.118 | 137.971
0.735 | 9349.677 | 139.31
0.74 | 8834.231 | 128.649
0.745 | 9206.135 | 147.905
0.75 | 9362.726 | 130.63
0.755 | 9441.021 | 139.825
0.76 | 8971.249 | 133.523
0.765 | 9049.544 | 137.866
0.77 | 9127.839 | 141.049
0.775 | 9206.135 | 135.26
0.78 | 9349.677 | 139.042
0.785 | 9069.118 | 136.446
0.79 | 8834.231 | 138.268
0.795 | 9029.97 | 144.968
0.8 | 9127.839 | 138.157
0.805 | 8051.277 | 139.313
0.81 | 7738.095 | 161.47
0.815 | 7013.862 | 157.227
0.82 | 3005.133 | 186.279
0.825 | 1865.934 | 260.261

## Test-7276
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7276
Scenario | 274 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 259.4
Arc Current (A) | 9223
Arc Voltage (V) | 123.8
Duration of Arc (s) | 1.185
Arc Energy (kJ) | 1245
Incident Energy at 450 mm Distance (cal/cm²) | 10.7
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | 69
Configuarion | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 259
0.085 | 8863.283 | 66.53 | 20000 | 0
0.09 | 12427.12 | 69.654
0.095 | 13122.624 | 68.873
0.1 | 13289.256 | 68.873
0.105 | 13386.963 | 64.969
0.11 | 13427.373 | 67.311
0.115 | 13426.634 | 66.53
0.12 | 13480.738 | 65.749
0.125 | 13845.236 | 57.16
0.13 | 14223.051 | 51.694
0.135 | 14441.948 | 52.475
0.14 | 14417.098 | 54.818
0.145 | 14185.782 | 57.941
0.15 | 14014.526 | 63.407
0.155 | 13822.159 | 64.188
0.16 | 13746.825 | 62.626
0.165 | 13683.534 | 64.188
0.17 | 13547.557 | 68.873
0.175 | 13349.454 | 70.434
0.18 | 13139.238 | 71.996
0.185 | 13037.186 | 73.558
0.19 | 13028.244 | 71.996
0.195 | 13062.252 | 71.215
0.2 | 13162.06 | 71.215
0.205 | 13163.877 | 66.53
0.21 | 13094.935 | 75.9
0.215 | 12912.052 | 75.119
0.22 | 12788.31 | 79.805
0.225 | 12743.577 | 75.119
0.23 | 12762.962 | 71.996
0.235 | 12846.428 | 75.9
0.24 | 12786.581 | 76.681
0.245 | 12661.876 | 79.024
0.25 | 12489.172 | 82.928
0.255 | 12321.276 | 85.27
0.26 | 12039.419 | 90.736
0.265 | 11806.284 | 88.394
0.27 | 11823.659 | 88.394
0.275 | 11894.634 | 86.051
0.28 | 12008.313 | 81.366
0.285 | 12076.108 | 89.955
0.29 | 11801.851 | 93.86
0.295 | 11750.679 | 86.051
0.3 | 11958.559 | 83.709
0.305 | 12029.624 | 86.051
0.31 | 11847.646 | 93.079
0.315 | 11635.652 | 91.517
0.32 | 11686.779 | 85.27
0.325 | 11849.088 | 88.394
0.33 | 11904.736 | 86.832
0.335 | 11905.479 | 86.832
0.34 | 11832.919 | 89.955
0.345 | 11686.187 | 91.517
0.35 | 11511.004 | 96.983
0.355 | 11329.017 | 96.983
0.36 | 11193.248 | 97.764
0.365 | 11106.742 | 100.887
0.37 | 11077.966 | 95.421
0.375 | 11095.331 | 96.983
0.38 | 11177.878 | 94.64
0.385 | 11219.572 | 96.202
0.39 | 11260.604 | 98.545
0.395 | 11293.087 | 92.298
0.4 | 11304.93 | 93.86
0.405 | 11258.8 | 96.202
0.41 | 11198.434 | 97.764
0.415 | 11199.851 | 95.421
0.42 | 11266.84 | 94.64
0.425 | 11299.769 | 96.202
0.43 | 11252.577 | 97.764
0.435 | 11187.175 | 97.764
0.44 | 11096.248 | 97.764
0.445 | 11049.943 | 99.325
0.45 | 11000.345 | 97.764
0.455 | 10960.127 | 98.545
0.46 | 10923.177 | 100.106
0.465 | 10832.103 | 104.791
0.47 | 10766.831 | 104.01
0.475 | 10705.041 | 104.791
0.48 | 10722.77 | 103.23
0.485 | 10776.103 | 100.106
0.49 | 10775.273 | 104.01
0.495 | 10715.218 | 103.23
0.5 | 10585.609 | 106.353
0.505 | 10487.703 | 110.257
0.51 | 10296.39 | 111.819
0.515 | 9944.808 | 123.531
0.52 | 9543.82 | 125.874
0.525 | 9328.484 | 126.655
0.53 | 9205.468 | 123.531
0.535 | 9191.897 | 125.093
0.54 | 9196.095 | 122.75
0.545 | 9190.065 | 126.655
0.55 | 9156.553 | 122.75
0.555 | 9122.973 | 128.216
0.56 | 9038.283 | 125.874
0.565 | 8972.9 | 127.435
0.57 | 9157.599 | 121.189
0.575 | 9362.707 | 111.819
0.58 | 9632.251 | 117.285
0.585 | 9738.893 | 114.161
0.59 | 9773.218 | 113.38
0.595 | 9795.088 | 118.846
0.6 | 9779.491 | 113.38
0.605 | 9890.304 | 110.257
0.61 | 9898.116 | 115.723
0.615 | 9866.242 | 116.504
0.62 | 9860.628 | 111.038
0.625 | 9913.691 | 113.38
0.63 | 9978.895 | 110.257
0.635 | 9935.416 | 116.504
0.64 | 9799.884 | 121.97
0.645 | 9443.09 | 121.97
0.65 | 9295.701 | 125.093
0.655 | 9279.536 | 121.189
0.66 | 9225.193 | 125.093
0.665 | 9175.72 | 127.435
0.67 | 9078.087 | 122.75
0.675 | 8963.04 | 130.559
0.68 | 8749.067 | 128.216
0.685 | 8630.529 | 132.901
0.69 | 8482.968 | 136.025
0.695 | 8245.927 | 142.271
0.7 | 8036.543 | 139.929
0.705 | 7858.936 | 153.984
0.71 | 7714.407 | 136.025
0.715 | 8098.221 | 134.463
0.72 | 8391.608 | 127.435
0.725 | 8748.481 | 132.12
0.73 | 8954.893 | 122.75
0.735 | 8951.453 | 125.874
0.74 | 8939.468 | 130.559
0.745 | 8945.016 | 133.682
0.75 | 8574.082 | 136.025
0.755 | 8218.343 | 142.271
0.76 | 8166.919 | 136.025
0.765 | 8038.843 | 143.052
0.77 | 7803.66 | 152.422
0.775 | 7400.432 | 157.888
0.78 | 6981.67 | 157.888
0.785 | 6496.71 | 232.067
0.79 | 3895.027 | 207.861
0.795 | 3053.035 | 219.574
0.8 | 3335.432 | 184.436
0.805 | 4363.993 | 171.162
0.81 | 5596.008 | 153.984
0.815 | 6738.46 | 138.367
0.82 | 7592.177 | 131.34
0.825 | 8271.249 | 137.586
0.83 | 8248.193 | 136.805
0.835 | 8237.763 | 136.805
0.84 | 8241.238 | 141.49
0.845 | 8144.744 | 134.463
0.85 | 7931.998 | 142.271
0.855 | 7962.106 | 134.463
0.86 | 8176.722 | 137.586
0.865 | 8267.636 | 130.559
0.87 | 8612.254 | 122.75
0.875 | 8918.558 | 141.49
0.88 | 8343.494 | 139.148
0.885 | 8165.615 | 143.052
0.89 | 8116.22 | 136.025
0.895 | 8072.796 | 143.833
0.9 | 8038.328 | 136.025
0.905 | 7769.637 | 161.792
0.91 | 6931.227 | 173.505
0.915 | 6278.507 | 171.162
0.92 | 5836.806 | 196.93
0.925 | 5244.086 | 188.341
0.93 | 4974.206 | 153.203
0.935 | 6513.097 | 132.12
0.94 | 7986.681 | 130.559
0.945 | 8311.595 | 138.367
0.95 | 8024.202 | 146.956
0.955 | 7869.28 | 135.244
0.96 | 8052.218 | 133.682
0.965 | 8093.558 | 136.805
0.97 | 8101.587 | 139.148
0.975 | 8057.76 | 139.148
0.98 | 8044.418 | 139.929
0.985 | 7993.539 | 143.052
0.99 | 7887.575 | 148.518
0.995 | 7445.149 | 154.765
1 | 7012.358 | 157.107
1.005 | 6943.249 | 149.299
1.01 | 6520.093 | 178.971
1.015 | 6115.051 | 167.258
1.02 | 5917.991 | 161.792
1.025 | 6135.96 | 166.477
1.03 | 5918.189 | 183.656
1.035 | 5843.188 | 150.86
1.04 | 6587.635 | 148.518
1.045 | 7058.413 | 147.737
1.05 | 7307.978 | 149.299
1.055 | 7341.405 | 144.614
1.06 | 7344.445 | 148.518
1.065 | 7356.147 | 146.956
1.07 | 7303.279 | 147.737
1.075 | 7248.091 | 149.299
1.08 | 7413.887 | 146.175
1.085 | 7493.189 | 149.299
1.09 | 7357.151 | 151.641
1.095 | 7250.886 | 143.052
1.1 | 7128.892 | 162.573
1.105 | 6871.579 | 151.641
1.11 | 6926.254 | 148.518
1.115 | 7314.832 | 137.586
1.12 | 7519.234 | 148.518
1.125 | 7216.053 | 161.792
1.13 | 6772.295 | 160.231
1.135 | 6899.873 | 146.175
1.14 | 7187.078 | 151.641
1.145 | 6928.361 | 167.258
1.15 | 6414.944 | 165.696
1.155 | 6217.937 | 185.217
1.16 | 5660.713 | 159.45
1.165 | 6512.823 | 144.614
1.17 | 7260.782 | 144.614
1.175 | 7523.604 | 143.052
1.18 | 6993.15 | 158.669
1.185 | 6565.187 | 166.477
1.19 | 6241.355 | 175.847
1.195 | 4833.78 | 223.087
1.2 | 4381.471 | 166.477
1.205 | 5075.407 | 182.875
1.21 | 5478.679 | 157.888
1.215 | 6231.986 | 147.737
1.22 | 6812.246 | 143.052
1.225 | 7131.055 | 164.135
1.23 | 6690.175 | 146.175
1.235 | 6968.676 | 143.052
1.24 | 7052.742 | 160.231
1.245 | 6747.91 | 160.231
1.25 | 6763.48 | 143.052
1.255 | 6935.775 | 234.02
1.26 | 4464.765 | 280.479

## Test-7277
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7277
Scenario | 274 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 259.8
Arc Current (A) | 10010
Arc Voltage (V) | 111.9
Duration of Arc (s) | 0.8562
Arc Energy (kJ) | 911.1
Incident Energy at 450 mm Distance (cal/cm²) | 8.01
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
|  |  | I | Vbat
Time (s) | Current (A) | Voltage (V) | 0 | 260
0.085 | 13137.075 | 56.477 | 20000 | 0
0.089 | 13339.567 | 64.756
0.094 | 13582.557 | 63.767
0.099 | 13582.557 | 63.842
0.104 | 13339.567 | 64.183
0.11 | 13258.57 | 66.86
0.114 | 13785.049 | 67.608
0.119 | 14028.039 | 61.699
0.124 | 14392.524 | 55.264
0.129 | 14352.026 | 52.845
0.134 | 13947.042 | 53.409
0.139 | 13866.045 | 56.788
0.144 | 13461.062 | 61.303
0.149 | 13420.563 | 64.318
0.155 | 13137.075 | 66.561
0.16 | 12732.091 | 71.575
0.165 | 12691.593 | 76.129
0.17 | 12691.593 | 77.654
0.174 | 13380.065 | 72.231
0.179 | 13339.567 | 64.623
0.185 | 12853.586 | 67.736
0.19 | 13056.078 | 70.635
0.195 | 12934.583 | 71.337
0.2 | 12691.593 | 71.547
0.205 | 12610.596 | 74.635
0.21 | 12084.117 | 79.764
0.215 | 12367.606 | 81.697
0.22 | 12246.11 | 80.747
0.225 | 12408.104 | 79.026
0.23 | 12003.12 | 81.231
0.236 | 11598.136 | 87.407
0.241 | 11638.635 | 89.264
0.246 | 11679.133 | 89.136
0.251 | 11638.635 | 88.739
0.256 | 11638.635 | 88.589
0.261 | 11841.127 | 88.178
0.266 | 11679.133 | 87.627
0.271 | 11314.648 | 90.149
0.276 | 10950.162 | 95.806
0.281 | 11071.657 | 98.961
0.286 | 11274.149 | 95.662
0.291 | 11395.644 | 92.247
0.296 | 11517.14 | 91.424
0.301 | 11760.13 | 89.369
0.306 | 11800.628 | 87.338
0.311 | 11274.149 | 88.931
0.316 | 11314.648 | 94.119
0.321 | 10828.667 | 98.37
0.326 | 10707.172 | 100.833
0.331 | 10869.166 | 101.14
0.337 | 10464.182 | 104.14
0.342 | 10342.687 | 105.79
0.347 | 10383.185 | 107.198
0.352 | 10261.69 | 106.507
0.356 | 10545.179 | 105.821
0.362 | 10383.185 | 103.448
0.366 | 10990.661 | 101.109
0.371 | 10990.661 | 96.391
0.376 | 10950.162 | 95.405
0.381 | 11274.149 | 95.316
0.386 | 10950.162 | 97.058
0.391 | 11152.654 | 96.824
0.396 | 10950.162 | 98.104
0.401 | 10707.172 | 99.259
0.406 | 10707.172 | 101.922
0.412 | 10342.687 | 105.499
0.417 | 10302.188 | 105.971
0.422 | 10423.683 | 106.045
0.427 | 10261.69 | 105.605
0.432 | 10261.69 | 108.109
0.437 | 9897.205 | 111.852
0.442 | 9694.713 | 115.724
0.447 | 9330.227 | 119.325
0.453 | 8884.745 | 124.724
0.457 | 9168.234 | 123.165
0.462 | 9613.716 | 116.219
0.467 | 9411.224 | 115.75
0.473 | 9006.24 | 127.084
0.478 | 8115.276 | 142.924
0.483 | 9046.739 | 118.111
0.487 | 9573.217 | 111.549
0.492 | 9897.205 | 109.895
0.497 | 10018.7 | 110.866
0.502 | 9694.713 | 114.04
0.507 | 9573.217 | 117.089
0.513 | 9046.739 | 123.57
0.518 | 8925.243 | 128.892
0.522 | 9330.227 | 117.476
0.528 | 8763.25 | 125.512
0.532 | 9249.23 | 125.06
0.537 | 9127.735 | 121.273
0.542 | 9451.722 | 118.48
0.547 | 10018.7 | 111.264
0.552 | 9735.211 | 112.924
0.557 | 9492.221 | 118.322
0.562 | 9249.23 | 121.06
0.568 | 9006.24 | 123.492
0.572 | 9451.722 | 113.125
0.578 | 9006.24 | 124.161
0.582 | 9694.713 | 117.78
0.587 | 9856.706 | 112.608
0.592 | 9897.205 | 112.34
0.597 | 9654.214 | 113.677
0.602 | 9613.716 | 115.354
0.607 | 9249.23 | 118.995
0.612 | 9532.719 | 120.06
0.617 | 9451.722 | 114.854
0.622 | 9411.224 | 117.57
0.627 | 9573.217 | 117.483
0.632 | 9654.214 | 114.157
0.637 | 9492.221 | 116.496
0.642 | 9573.217 | 117.204
0.647 | 9492.221 | 118.027
0.653 | 9006.24 | 123.005
0.658 | 8601.256 | 135.476
0.663 | 8682.253 | 125.774
0.668 | 8803.748 | 126.287
0.673 | 8763.25 | 128.583
0.678 | 8034.279 | 136.557
0.683 | 8560.758 | 133.101
0.688 | 8479.761 | 130.361
0.692 | 9168.234 | 125.587
0.697 | 9127.735 | 120.712
0.703 | 9006.24 | 123.893
0.707 | 9775.709 | 117.16
0.712 | 9573.217 | 115.246
0.717 | 9411.224 | 116.849
0.723 | 8601.256 | 128.808
0.728 | 8398.765 | 132.521
0.733 | 9087.237 | 121.69
0.738 | 8763.25 | 126.768
0.743 | 8884.745 | 125.714
0.747 | 9411.224 | 122.249
0.753 | 8925.243 | 123.699
0.758 | 8925.243 | 126.507
0.763 | 8965.742 | 125.541
0.768 | 8803.748 | 127.604
0.773 | 8439.263 | 129.938
0.778 | 8884.745 | 127.703
0.783 | 8479.761 | 129.075
0.788 | 8763.25 | 127.357
0.793 | 9046.739 | 122.512
0.797 | 9289.729 | 120.186
0.803 | 8520.26 | 126.827
0.808 | 8520.26 | 133.617
0.813 | 8479.761 | 128.788
0.818 | 8844.247 | 127.649
0.823 | 8601.256 | 130.95
0.828 | 8236.771 | 132.812
0.833 | 8479.761 | 131.383
0.838 | 8560.758 | 128.913
0.843 | 8722.752 | 128.504
0.848 | 8398.765 | 132.189
0.853 | 8115.276 | 140.689
0.858 | 7912.784 | 137.795
0.863 | 8155.774 | 139.43
0.869 | 7629.295 | 142.327
0.873 | 8074.778 | 137.378
0.878 | 7831.787 | 139.101
0.883 | 7872.286 | 140.721
0.889 | 7669.794 | 155.92
0.894 | 6495.341 | 194.724
0.9 | 5442.383 | 207.854
0.901 | 4308.429 | 201.773
0.903 | 2000.021 | 191.45
0.907 | 3295.969 | 179.747
0.911 | 3781.95 | 167.217
0.915 | 5725.872 | 155.779
0.919 | 6454.842 | 186.655
0.925 | 6171.354 | 278.616
0.926 | 4389.425 | 288.411
0.927 | 2283.51 | 292.253

## Test-7278
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7278
Scenario | 274 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 259.3
Arc Current (A) | 8585
Arc Voltage (V) | 131.6
Duration of Arc (s) | 1.35
Arc Energy (kJ) | 1377
Incident Energy at 450 mm Distance (cal/cm²) | 10.3
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline |  | I | Vbat
|  |  | 0 | 260
Time (s) | Current (A) | Voltage (V) | 20000 | 0
0.085 | 12566.707 | 71.368
0.09 | 12965.209 | 70.338
0.095 | 13124.61 | 71.157
0.1 | 13323.861 | 71.663
0.105 | 13602.812 | 66.636
0.11 | 13682.512 | 63.586
0.115 | 13881.763 | 60.343
0.12 | 13881.763 | 59.32
0.125 | 14120.864 | 58.333
0.13 | 14120.864 | 54.48
0.135 | 13802.063 | 54.451
0.14 | 13722.362 | 57.123
0.145 | 13323.861 | 60.172
0.15 | 13323.861 | 63.924
0.155 | 13642.662 | 67.948
0.16 | 13323.861 | 63.133
0.165 | 13284.01 | 61.765
0.17 | 13244.16 | 67.476
0.175 | 13204.31 | 66.212
0.18 | 13124.61 | 65.408
0.185 | 12925.359 | 68.975
0.19 | 13005.059 | 70.604
0.195 | 12845.658 | 68.163
0.2 | 13005.059 | 70.702
0.205 | 12925.359 | 73.238
0.21 | 12646.407 | 69.522
0.215 | 12805.808 | 73.416
0.22 | 12367.456 | 73.415
0.225 | 12487.007 | 73.539
0.23 | 12367.456 | 78.651
0.235 | 12088.505 | 77.254
0.24 | 12247.906 | 80.657
0.245 | 12247.906 | 79.379
0.25 | 12088.505 | 81.058
0.255 | 11968.954 | 79.336
0.26 | 11769.703 | 82.173
0.265 | 12048.655 | 84.048
0.27 | 11929.104 | 85.282
0.275 | 11889.254 | 83.379
0.28 | 11809.554 | 83.871
0.285 | 11251.651 | 84.334
0.29 | 11371.202 | 89.401
0.295 | 11211.801 | 93.542
0.3 | 11171.951 | 94.105
0.305 | 11490.752 | 93.105
0.31 | 11411.052 | 92.706
0.315 | 11690.003 | 89.326
0.32 | 11171.951 | 89.927
0.325 | 11052.4 | 89.892
0.33 | 11092.25 | 97.941
0.335 | 10892.999 | 97.646
0.34 | 10972.7 | 96.822
0.345 | 10653.898 | 98.608
0.35 | 10574.198 | 97.685
0.355 | 10733.599 | 105.418
0.36 | 10574.198 | 102.978
0.365 | 10932.85 | 102.109
0.37 | 10892.999 | 100.865
0.375 | 10932.85 | 99.716
0.38 | 10892.999 | 96.351
0.385 | 10813.299 | 99.087
0.39 | 10773.449 | 100.018
0.395 | 10414.797 | 96.693
0.4 | 10534.348 | 107.704
0.405 | 10414.797 | 110.228
0.41 | 10454.647 | 104.566
0.415 | 10932.85 | 109.052
0.42 | 10813.299 | 102.358
0.425 | 10853.149 | 98.229
0.43 | 10853.149 | 102.754
0.435 | 10534.348 | 99.605
0.44 | 10374.947 | 102.872
0.445 | 10255.396 | 107.613
0.45 | 10733.599 | 108.862
0.455 | 10534.348 | 107.091
0.46 | 10534.348 | 101.617
0.465 | 10414.797 | 108.391
0.471 | 9697.494 | 103.386
0.476 | 9458.393 | 115.207
0.481 | 9458.393 | 119.02
0.486 | 9020.041 | 121.475
0.491 | 9219.292 | 124.422
0.496 | 9139.591 | 126.956
0.501 | 9538.093 | 118.703
0.506 | 9179.441 | 127.282
0.511 | 9020.041 | 119.423
0.516 | 9259.142 | 130.517
0.521 | 8860.64 | 122.125
0.526 | 8422.288 | 122.894
0.531 | 9179.441 | 135.023
0.536 | 9418.543 | 133.577
0.541 | 9298.992 | 115.738
0.546 | 9378.692 | 119.554
0.551 | 9697.494 | 131.107
0.556 | 9817.044 | 116.796
0.56 | 10414.797 | 114.138
0.565 | 10056.145 | 111.435
0.571 | 9418.543 | 105.889
0.576 | 9577.943 | 124.718
0.58 | 10095.996 | 119.498
0.586 | 9577.943 | 114.48
0.591 | 9617.793 | 113.253
0.596 | 9538.093 | 119.238
0.601 | 9657.644 | 118.38
0.606 | 9936.595 | 118.782
0.611 | 9817.044 | 115.094
0.616 | 9657.644 | 112.16
0.621 | 9498.243 | 116.23
0.626 | 9458.393 | 120.193
0.631 | 9338.842 | 117.521
0.636 | 9219.292 | 120.68
0.641 | 9777.194 | 120.405
0.646 | 9737.344 | 121.028
0.651 | 9418.543 | 111.293
0.656 | 9219.292 | 116.354
0.661 | 9219.292 | 121.566
0.666 | 9538.093 | 124.192
0.671 | 9617.793 | 120.984
0.676 | 9378.692 | 116.458
0.681 | 9657.644 | 119.333
0.686 | 9298.992 | 119.646
0.691 | 9099.741 | 119.042
0.696 | 9298.992 | 120.987
0.701 | 9099.741 | 124.029
0.706 | 8262.887 | 118.704
0.711 | 7784.685 | 133.906
0.716 | 7784.685 | 146.88
0.721 | 7505.734 | 140.071
0.726 | 5752.326 | 149.278
0.731 | 5752.326 | 156.089
0.736 | 6469.629 | 200.227
0.741 | 7226.782 | 158.737
0.746 | 4516.97 | 152.673
0.751 | 4716.221 | 161.337
0.756 | 5672.625 | 203.165
0.761 | 7067.382 | 184.042
0.766 | 7704.985 | 146.581
0.771 | 7824.535 | 147.684
0.776 | 8223.037 | 134.621
0.781 | 8422.288 | 139.706
0.786 | 8342.588 | 135.849
0.791 | 8701.239 | 132.129
0.796 | 9099.741 | 129.493
0.801 | 8980.19 | 126.268
0.806 | 8501.988 | 123.893
0.811 | 9020.041 | 133.539
0.816 | 8541.838 | 127.101
0.821 | 8103.486 | 128.511
0.826 | 8223.037 | 142.483
0.831 | 8621.539 | 137.492
0.836 | 8023.786 | 131.21
0.841 | 7944.086 | 133.956
0.846 | 8741.089 | 147.212
0.851 | 8302.737 | 128.592
0.856 | 8223.037 | 130.238
0.861 | 8143.337 | 140.46
0.866 | 8143.337 | 135.111
0.871 | 7465.883 | 140.195
0.876 | 7426.033 | 146.131
0.881 | 7226.782 | 149.006
0.886 | 6071.127 | 153.021
0.891 | 6071.127 | 153.254
0.896 | 6509.479 | 204.758
0.901 | 4955.322 | 157.777
0.902 | 3042.513 | 153.381
0.906 | 4955.322 | 162.914
0.911 | 4676.371 | 234.123
0.917 | 3042.513 | 179.126
0.922 | 3002.663 | 204.334
0.926 | 5971.501 | 225.011
0.931 | 8143.337 | 179.921
0.936 | 8661.389 | 140.998
0.941 | 8302.737 | 124.324
0.946 | 7983.936 | 131.441
0.951 | 8223.037 | 143.985
0.956 | 8183.187 | 137.454
0.961 | 7944.086 | 136.89
0.966 | 7784.685 | 140.815
0.971 | 7426.033 | 137.214
0.976 | 6947.831 | 144.348
0.981 | 7186.932 | 158.282
0.986 | 7186.932 | 152.761
0.991 | 7147.082 | 149.594
0.996 | 6310.228 | 149.989
1.001 | 6110.977 | 158.515
1.007 | 4158.318 | 171.77
1.011 | 5194.423 | 177.568
1.012 | 3241.764 | 183.639
1.016 | 6629.03 | 213.627
1.021 | 7744.835 | 160.37
1.026 | 8422.288 | 139.435
1.031 | 8143.337 | 131.184
1.036 | 8262.887 | 134.408
1.041 | 8023.786 | 139.738
1.046 | 7704.985 | 132.278
1.051 | 8063.636 | 151.008
1.056 | 8223.037 | 137.345
1.061 | 7824.535 | 139.438
1.066 | 6868.131 | 140.378
1.071 | 6110.977 | 153.494
1.076 | 7465.883 | 174.604
1.081 | 8262.887 | 162.016
1.086 | 7704.985 | 134.262
1.091 | 7585.434 | 140.954
1.096 | 7386.183 | 151.188
1.101 | 6509.479 | 139.834
1.106 | 5752.326 | 158.921
1.107 | 3759.816 | 162.203
1.111 | 6270.378 | 173.706
1.116 | 7784.685 | 201.166
1.121 | 8382.438 | 138.065
1.126 | 8223.037 | 128.381
1.131 | 7306.483 | 131.034
1.136 | 7505.734 | 154.374
1.141 | 6828.28 | 148.888
1.146 | 6788.43 | 152.483
1.151 | 6788.43 | 158.992
1.156 | 6629.03 | 160.267
1.161 | 6589.179 | 156.066
1.166 | 6350.078 | 161.773
1.171 | 6828.28 | 164.643
1.176 | 6549.329 | 159.306
1.181 | 6350.078 | 157.92
1.186 | 6071.127 | 164.894
1.191 | 5991.427 | 166.318
1.196 | 5592.925 | 171.235
1.202 | 3122.213 | 175.507
1.206 | 4955.322 | 181.858
1.211 | 6549.329 | 204.484
1.212 | 4277.869 | 188.743
1.217 | 2046.258 | 155.83
1.232 | 1926.708 | 238.603
1.237 | 2404.91 | 209.5
1.242 | 3919.217 | 230.876
1.246 | 5832.026 | 208.249
1.251 | 6549.329 | 189.505
1.256 | 6907.981 | 150.46
1.261 | 7266.633 | 158.249
1.266 | 7585.434 | 154.267
1.271 | 7904.235 | 143.377
1.276 | 7665.134 | 141.306
1.281 | 7386.183 | 142.441
1.286 | 7545.584 | 154.725
1.291 | 7186.932 | 150.21
1.296 | 6668.88 | 148.468
1.301 | 6987.681 | 161.975
1.306 | 7107.232 | 160.555
1.311 | 6668.88 | 155.113
1.316 | 6629.03 | 155.024
1.321 | 7107.232 | 183.416
1.326 | 6469.629 | 149.535
1.331 | 5672.625 | 160.036
1.336 | 5911.726 | 172.044
1.341 | 6110.977 | 178.206
1.346 | 6788.43 | 166.662
1.351 | 6788.43 | 168.776
1.356 | 6150.827 | 156.142
1.361 | 5632.775 | 167.463
1.366 | 5154.573 | 173.642
1.371 | 5672.625 | 190.423
1.376 | 6708.73 | 181.797
1.381 | 5951.576 | 160.731
1.386 | 6150.827 | 171.276
1.391 | 6748.58 | 173.13
1.396 | 6589.179 | 160.216
1.401 | 5871.876 | 159.294
1.407 | 3361.314 | 168.913
1.412 | 2006.408 | 193.033

## Test-7279
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7279
Scenario | 500 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 520.3
Arc Current (A) | 10940
Arc Voltage (V) | 182.7
Duration of Arc (s) | 1.999
Arc Energy (kJ) | 3726
Incident Energy at 450 mm Distance (cal/cm²) | 48.1
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V)
0.115 | 9238.8517 | 64.957
0.12 | 15589.525 | 62.531
0.125 | 15552.441 | 63.744
0.13 | 15849.115 | 67.384
0.135 | 15441.188 | 67.384
0.14 | 15663.694 | 61.317
0.145 | 15886.199 | 63.744
0.15 | 15700.778 | 60.104
0.155 | 15960.368 | 61.317
0.16 | 15589.525 | 60.104
0.165 | 15774.947 | 61.317
0.17 | 15774.947 | 66.17
0.175 | 15441.188 | 64.957
0.18 | 15812.031 | 63.744
0.185 | 15367.02 | 69.81
0.19 | 15404.104 | 67.384
0.195 | 15589.525 | 71.023
0.2 | 15218.683 | 72.237
0.205 | 15515.357 | 73.45
0.21 | 15144.515 | 73.45
0.215 | 15255.767 | 69.81
0.22 | 15515.357 | 72.237
0.225 | 15181.599 | 73.45
0.23 | 15255.767 | 80.729
0.235 | 14847.841 | 86.796
0.24 | 14662.42 | 85.582 | I | Vbat
0.245 | 14996.178 | 85.582 | 0 | 520
0.25 | 14847.841 | 77.09 | 20000 | 0
0.255 | 15107.43 | 81.943
0.26 | 14922.009 | 84.369
0.265 | 14588.251 | 91.649
0.27 | 14662.42 | 94.075
0.275 | 14217.409 | 95.288
0.28 | 14588.251 | 95.288
0.285 | 14773.672 | 84.369
0.29 | 14551.167 | 86.796
0.295 | 14699.504 | 92.862
0.3 | 14328.662 | 96.502
0.305 | 14291.578 | 96.502
0.31 | 14699.504 | 91.649
0.315 | 14254.493 | 94.075
0.32 | 14588.251 | 95.288
0.325 | 14402.83 | 92.862
0.33 | 14365.746 | 97.715
0.335 | 14514.083 | 97.715
0.34 | 14143.241 | 96.502
0.345 | 14439.914 | 97.715
0.35 | 14254.493 | 97.715
0.355 | 14254.493 | 96.502
0.36 | 14402.83 | 95.288
0.365 | 14069.072 | 100.141
0.37 | 14328.662 | 95.288
0.375 | 14254.493 | 98.928
0.38 | 13994.904 | 104.994
0.385 | 14069.072 | 106.208
0.39 | 13883.651 | 102.568
0.395 | 14069.072 | 104.994
0.4 | 13920.735 | 111.061
0.405 | 13809.483 | 104.994
0.41 | 13994.904 | 108.634
0.415 | 13735.314 | 108.634
0.42 | 13735.314 | 109.847
0.425 | 13772.398 | 112.274
0.43 | 13586.977 | 109.847
0.435 | 13772.398 | 113.487
0.44 | 13661.146 | 111.061
0.445 | 13327.388 | 123.193
0.45 | 13735.314 | 111.061
0.455 | 13401.556 | 118.34
0.46 | 13549.893 | 118.34
0.465 | 13438.64 | 121.98
0.47 | 13179.051 | 121.98
0.475 | 13438.64 | 120.767
0.48 | 12919.461 | 131.686
0.485 | 12993.63 | 130.473
0.49 | 12808.209 | 137.752
0.495 | 12659.872 | 138.965
0.5 | 12808.209 | 141.392
0.505 | 12734.04 | 135.326
0.51 | 12474.45 | 146.245
0.515 | 12808.209 | 134.112
0.52 | 12993.63 | 119.553
0.525 | 13586.977 | 115.914
0.53 | 13216.135 | 126.833
0.535 | 12993.63 | 126.833
0.54 | 13216.135 | 123.193
0.545 | 12919.461 | 131.686
0.55 | 13216.135 | 126.833
0.555 | 12734.04 | 138.965
0.56 | 12363.198 | 151.098
0.565 | 12251.945 | 152.311
0.57 | 12289.029 | 145.032
0.575 | 12400.282 | 153.524
0.58 | 12659.872 | 137.752
0.585 | 12326.114 | 151.098
0.59 | 12363.198 | 148.671
0.595 | 11992.356 | 159.59
0.6 | 12326.114 | 143.818
0.605 | 12548.619 | 142.605
0.61 | 12511.535 | 138.965
0.615 | 12734.04 | 141.392
0.62 | 12474.45 | 136.539
0.625 | 12251.945 | 151.098
0.63 | 12474.45 | 141.392
0.635 | 12326.114 | 146.245
0.64 | 12400.282 | 151.098
0.645 | 12103.608 | 146.245
0.65 | 12585.703 | 134.112
0.655 | 12548.619 | 148.671
0.66 | 12066.524 | 151.098
0.665 | 12363.198 | 145.032
0.67 | 11992.356 | 151.098
0.675 | 12103.608 | 158.377
0.68 | 11955.271 | 152.311
0.685 | 11769.85 | 160.804
0.69 | 12140.692 | 151.098
0.695 | 12140.692 | 152.311
0.7 | 11955.271 | 151.098
0.705 | 12177.777 | 154.737
0.71 | 12066.524 | 152.311
0.715 | 12029.44 | 158.377
0.72 | 11769.85 | 157.164
0.725 | 11806.934 | 164.443
0.73 | 11918.187 | 164.443
0.735 | 11065.25 | 174.149
0.74 | 11732.766 | 165.657
0.745 | 11436.092 | 169.296
0.75 | 11436.092 | 166.87
0.755 | 11621.513 | 169.296
0.76 | 11213.587 | 174.149
0.765 | 11547.345 | 168.083
0.77 | 12029.44 | 147.458
0.775 | 11621.513 | 160.804
0.78 | 11844.019 | 162.017
0.785 | 11658.598 | 148.671
0.79 | 11918.187 | 164.443
0.795 | 11695.682 | 160.804
0.8 | 11621.513 | 159.59
0.805 | 11992.356 | 159.59
0.81 | 11287.755 | 175.363
0.815 | 11547.345 | 163.23
0.82 | 11324.84 | 179.002
0.825 | 11584.429 | 155.951
0.83 | 11658.598 | 165.657
0.835 | 11361.924 | 169.296
0.84 | 11584.429 | 164.443
0.845 | 12029.44 | 158.377
0.85 | 11287.755 | 162.017
0.855 | 11769.85 | 169.296
0.86 | 11324.84 | 172.936
0.865 | 11287.755 | 174.149
0.87 | 11399.008 | 175.363
0.875 | 11139.418 | 172.936
0.88 | 11510.261 | 165.657
0.885 | 10991.082 | 187.495
0.89 | 10953.997 | 179.002
0.895 | 11436.092 | 172.936
0.9 | 10916.913 | 180.216
0.905 | 11139.418 | 176.576
0.91 | 10805.66 | 192.348
0.915 | 10805.66 | 179.002
0.92 | 10731.492 | 198.414
0.925 | 10879.829 | 181.429
0.93 | 10953.997 | 181.429
0.935 | 10694.408 | 193.561
0.94 | 10471.902 | 188.708
0.945 | 11287.755 | 172.936
0.95 | 11176.503 | 170.51
0.955 | 11361.924 | 166.87
0.96 | 11547.345 | 165.657
0.965 | 10731.492 | 189.922
0.97 | 10879.829 | 187.495
0.975 | 11361.924 | 170.51
0.98 | 11065.25 | 171.723
0.985 | 11139.418 | 177.789
0.99 | 10916.913 | 175.363
0.995 | 11028.166 | 179.002
1 | 10768.576 | 188.708
1.005 | 10805.66 | 182.642
1.01 | 10842.745 | 185.069
1.015 | 10842.745 | 185.069
1.02 | 11213.587 | 169.296
1.025 | 10805.66 | 191.135
1.03 | 10694.408 | 186.282
1.035 | 10842.745 | 182.642
1.04 | 11436.092 | 164.443
1.045 | 11213.587 | 171.723
1.05 | 11139.418 | 175.363
1.055 | 11176.503 | 180.216
1.06 | 10842.745 | 181.429
1.065 | 11065.25 | 180.216
1.07 | 10657.323 | 185.069
1.075 | 10620.239 | 195.988
1.08 | 10471.902 | 192.348
1.085 | 10323.565 | 198.414
1.09 | 10546.071 | 193.561
1.095 | 10360.65 | 200.841
1.1 | 10286.481 | 200.841
1.105 | 10212.313 | 202.054
1.11 | 9656.049 | 255.437
1.115 | 9989.807 | 204.481
1.12 | 10768.576 | 179.002
1.125 | 10805.66 | 187.495
1.13 | 10434.818 | 187.495
1.135 | 10434.818 | 197.201
1.14 | 10694.408 | 188.708
1.145 | 10397.734 | 192.348
1.15 | 10731.492 | 191.135
1.155 | 10249.397 | 199.628
1.16 | 10434.818 | 194.775
1.165 | 10249.397 | 198.414
1.17 | 10583.155 | 185.069
1.175 | 10508.987 | 200.841
1.18 | 10249.397 | 188.708
1.185 | 10360.65 | 199.628
1.19 | 10471.902 | 191.135
1.195 | 10175.229 | 194.775
1.2 | 10657.323 | 192.348
1.205 | 10212.313 | 198.414
1.21 | 10471.902 | 187.495
1.215 | 10768.576 | 179.002
1.22 | 10360.65 | 200.841
1.225 | 10286.481 | 198.414
1.23 | 10286.481 | 202.054
1.235 | 10323.565 | 195.988
1.24 | 10323.565 | 199.628
1.245 | 9804.386 | 206.907
1.25 | 10657.323 | 186.282
1.255 | 10212.313 | 205.694
1.26 | 10063.976 | 194.775
1.265 | 10546.071 | 195.988
1.27 | 10026.892 | 202.054
1.275 | 10286.481 | 202.054
1.28 | 10286.481 | 198.414
1.285 | 9730.218 | 215.4
1.29 | 10138.144 | 200.841
1.295 | 9804.386 | 210.547
1.3 | 10138.144 | 204.481
1.305 | 9989.807 | 214.187
1.31 | 9841.471 | 204.481
1.315 | 10101.06 | 202.054
1.32 | 10101.06 | 193.561
1.325 | 10471.902 | 189.922
1.33 | 10694.408 | 189.922
1.335 | 10063.976 | 199.628
1.34 | 10249.397 | 202.054
1.345 | 9804.386 | 212.973
1.35 | 9989.807 | 205.694
1.355 | 10249.397 | 206.907
1.36 | 9878.555 | 204.481
1.365 | 9656.049 | 220.253
1.37 | 9656.049 | 216.613
1.375 | 9581.881 | 214.187
1.38 | 9989.807 | 210.547
1.385 | 9433.544 | 220.253
1.39 | 9693.134 | 216.613
1.395 | 9841.471 | 208.12
1.4 | 9804.386 | 211.76
1.405 | 9544.797 | 223.893
1.41 | 9211.039 | 223.893
1.415 | 9544.797 | 215.4
1.42 | 9359.376 | 226.319
1.425 | 9136.87 | 239.665
1.43 | 8840.196 | 242.0915
1.435 | 9470.628 | 216.613
1.44 | 9618.965 | 216.613
1.445 | 9841.471 | 211.76
1.45 | 9470.628 | 220.253
1.455 | 10026.892 | 199.628
1.46 | 9989.807 | 204.481
1.465 | 9804.386 | 211.76
1.47 | 9656.049 | 217.826
1.475 | 9804.386 | 209.334
1.48 | 9841.471 | 209.334
1.485 | 9767.302 | 215.4
1.49 | 9693.134 | 210.547
1.495 | 10063.976 | 205.694
1.5 | 9804.386 | 203.267
1.505 | 9767.302 | 216.613
1.51 | 9767.302 | 210.547
1.515 | 9656.049 | 212.973
1.52 | 9767.302 | 210.547
1.525 | 9470.628 | 219.04
1.53 | 9618.965 | 216.613
1.535 | 9730.218 | 220.253
1.54 | 9507.713 | 215.4
1.545 | 9581.881 | 225.106
1.55 | 9025.618 | 237.238
1.555 | 8951.449 | 249.371
1.56 | 7171.406 | 314.28
1.565 | 7171.406 | 298.5075
1.57 | 8358.102 | 238.452
1.575 | 9099.786 | 227.532
1.58 | 8506.438 | 253.011
1.585 | 8617.691 | 240.878
1.59 | 8877.281 | 231.172
1.595 | 9211.039 | 229.959
1.6 | 9025.618 | 239.665
1.605 | 8877.281 | 231.172
1.61 | 8395.186 | 262.717
1.615 | 6911.817 | 339.758
1.62 | 6207.216 | 324.9967
1.625 | 8506.438 | 238.452
1.63 | 8951.449 | 229.959
1.635 | 9285.207 | 221.466
1.64 | 9359.376 | 227.532
1.645 | 6652.227 | 325.806
1.65 | 8766.028 | 219.04
1.655 | 9285.207 | 220.253
1.66 | 9656.049 | 215.4
1.665 | 9470.628 | 216.613
1.67 | 9470.628 | 219.04
1.675 | 9248.123 | 231.172
1.68 | 9173.954 | 225.106
1.685 | 9136.87 | 238.452
1.69 | 9396.46 | 220.253
1.695 | 9248.123 | 225.106
1.7 | 9359.376 | 222.679
1.705 | 9173.954 | 222.679
1.71 | 9322.291 | 227.532
1.715 | 8914.365 | 233.599
1.72 | 8877.281 | 236.025
1.725 | 8877.281 | 236.025
1.73 | 8914.365 | 231.172
1.735 | 8951.449 | 254.224
1.74 | 6503.89 | 322.166
1.745 | 5613.869 | 359.777
1.75 | 7134.322 | 292.441
1.755 | 8617.691 | 228.746
1.76 | 9248.123 | 231.172
1.765 | 9099.786 | 227.532
1.77 | 9173.954 | 226.319
1.775 | 9396.46 | 219.04
1.78 | 9173.954 | 223.893
1.785 | 9322.291 | 223.893
1.79 | 9433.544 | 214.187
1.795 | 9211.039 | 232.385
1.8 | 9062.702 | 236.025
1.805 | 8803.112 | 228.746
1.81 | 9396.46 | 221.466
1.815 | 9470.628 | 223.893
1.82 | 8988.533 | 233.599
1.825 | 9248.123 | 228.746
1.83 | 8951.449 | 231.172
1.835 | 8914.365 | 234.812
1.84 | 6837.648 | 327.6255
1.845 | 7060.154 | 259.077
1.85 | 8691.86 | 242.091
1.855 | 8654.775 | 239.665
1.86 | 8321.017 | 250.584
1.865 | 8617.691 | 250.584
1.87 | 8469.354 | 249.371
1.875 | 7152.8645 | 323.9855
1.88 | 6318.469 | 312.46
1.885 | 8172.68 | 243.305
1.89 | 8728.944 | 244.518
1.895 | 8840.196 | 231.172
1.9 | 8840.196 | 236.025
1.905 | 8654.775 | 254.224
1.91 | 6911.817 | 288.195
1.915 | 8172.68 | 254.224
1.92 | 8209.765 | 253.011
1.925 | 7616.417 | 289.408
1.93 | 6058.88 | 341.578
1.935 | 6133.048 | 305.787
1.94 | 8617.691 | 238.452
1.945 | 8691.86 | 242.091
1.95 | 9248.123 | 225.106
1.955 | 8580.607 | 248.158
1.96 | 7430.996 | 295.474
1.965 | 7505.164 | 280.915
1.97 | 7690.585 | 285.162
1.975 | 8432.27 | 236.025
1.98 | 8728.944 | 243.305
1.985 | 7060.1535 | 403.454
1.99 | 5502.6165 | 323.38
1.995 | 8395.186 | 237.238
2 | 8877.281 | 233.599
2.005 | 8840.196 | 240.878
2.01 | 8543.523 | 239.665
2.015 | 9211.039 | 226.319
2.02 | 9099.786 | 231.172
2.025 | 8617.691 | 242.091
2.03 | 8580.607 | 261.503
2.035 | 7393.912 | 285.768
2.04 | 8098.512 | 259.077
2.045 | 6633.685 | 430.145
2.05 | 7468.08 | 254.224
2.055 | 8951.449 | 237.238
2.06 | 8840.196 | 239.665
2.065 | 8766.028 | 239.665
2.07 | 8691.86 | 243.305
2.075 | 8654.775 | 243.305
2.08 | 9025.618 | 232.385
2.085 | 9470.628 | 255.437
2.09 | 6058.8797 | 368.269

## Test-7280
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7280
Scenario | 500 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 520.5
Arc Current (A) | 10890
Arc Voltage (V) | 184.2
Duration of Arc (s) | 2.004
Arc Energy (kJ) | 3772
Incident Energy at 450 mm Distance (cal/cm²) | 48.2
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | -
Configuration | inline
Time (s) | Current (A) | Voltage (V)
0.11 | 9578.222 | 22.588
0.115 | 15882.793 | 45.976 | I | Vbat
0.12 | 15976.891 | 56.74 | 0 | 520
0.125 | 15976.891 | 57.154 | 20000 | 0
0.13 | 16070.989 | 56.951
0.135 | 15788.695 | 57.036
0.14 | 16070.989 | 58.059
0.145 | 15929.842 | 59.234
0.15 | 15647.548 | 60.58
0.155 | 15788.695 | 61.628
0.16 | 15882.793 | 61.117
0.165 | 16118.038 | 59.534
0.17 | 16118.038 | 57.587
0.175 | 15835.744 | 57.394
0.18 | 15788.695 | 59.879
0.185 | 15318.205 | 65.227
0.19 | 15224.107 | 69.532
0.195 | 15365.254 | 72.139
0.2 | 15224.107 | 73.255
0.205 | 15506.401 | 73.526
0.21 | 15035.91 | 75.308
0.215 | 15177.058 | 77.978
0.22 | 15130.009 | 79.822
0.225 | 14988.861 | 81.634
0.23 | 15177.058 | 82.002
0.235 | 14847.714 | 81.364
0.24 | 14894.763 | 83.495
0.245 | 14565.42 | 86.361
0.25 | 14518.371 | 89.449
0.255 | 14565.42 | 93.488
0.26 | 14141.979 | 96.818
0.265 | 14377.224 | 98.745
0.27 | 14236.077 | 101.727
0.275 | 14094.93 | 104.356
0.28 | 14047.881 | 104.239
0.285 | 14189.028 | 102.59
0.29 | 14565.42 | 100.937
0.295 | 14424.273 | 97.777
0.3 | 14236.077 | 97.149
0.305 | 14330.175 | 98.192
0.31 | 14141.979 | 97.962
0.315 | 14424.273 | 98.276
0.32 | 14000.832 | 99.378
0.325 | 14000.832 | 101.699
0.33 | 13718.537 | 107.213
0.335 | 13153.949 | 115.908
0.34 | 13530.341 | 122.18
0.345 | 13295.096 | 125.031
0.35 | 13248.047 | 126.39
0.355 | 13342.145 | 125.886
0.36 | 13248.047 | 126.502
0.365 | 13577.39 | 124.373
0.37 | 13436.243 | 121.161
0.375 | 13577.39 | 118.252
0.38 | 13859.684 | 113.827
0.385 | 13859.684 | 111.659
0.39 | 13812.635 | 110.406
0.395 | 13671.488 | 109.205
0.4 | 13906.733 | 110.568
0.405 | 13671.488 | 112.438
0.41 | 13483.292 | 112.845
0.415 | 13812.635 | 114.264
0.42 | 13718.537 | 114.399
0.425 | 13671.488 | 114.426
0.43 | 13624.439 | 115.119
0.435 | 13530.341 | 115.274
0.44 | 13671.488 | 116.984
0.445 | 13483.292 | 118.853
0.45 | 13153.949 | 119.096
0.455 | 13577.39 | 117.752
0.46 | 13577.39 | 118.589
0.465 | 13530.341 | 117.489
0.47 | 13295.096 | 117.261
0.475 | 13483.292 | 120.66
0.48 | 13295.096 | 124.059
0.485 | 12824.606 | 126.455
0.49 | 13200.998 | 130.119
0.495 | 12730.507 | 133.91
0.5 | 12589.36 | 137.507
0.505 | 12401.164 | 143.689
0.51 | 12024.772 | 147.262
0.515 | 12448.213 | 150.334
0.52 | 12260.017 | 151.711
0.525 | 12307.066 | 151.248
0.53 | 12354.115 | 149.718
0.535 | 12212.968 | 149.157
0.54 | 12589.36 | 147.046
0.545 | 12683.458 | 141.526
0.55 | 13200.998 | 136.838
0.555 | 13012.802 | 131.596
0.56 | 12542.311 | 133.635
0.565 | 12871.655 | 136.908
0.57 | 12448.213 | 139.156
0.575 | 12589.36 | 140.597
0.58 | 12495.262 | 140.773
0.585 | 12589.36 | 140.428
0.59 | 12777.557 | 139.589
0.595 | 12448.213 | 137.893
0.6 | 12918.704 | 137.333
0.605 | 12448.213 | 139.419
0.61 | 12448.213 | 141.333
0.615 | 12401.164 | 144.3
0.62 | 12118.87 | 149.256
0.625 | 12212.968 | 151.397
0.63 | 11977.723 | 156.09
0.635 | 11507.232 | 157.317
0.64 | 11930.674 | 160.621
0.645 | 12118.87 | 156.967
0.65 | 12260.017 | 153.076
0.655 | 12260.017 | 148.897
0.66 | 12542.311 | 146.077
0.665 | 12307.066 | 144.554
0.67 | 12354.115 | 144.889
0.675 | 12165.919 | 145.117
0.68 | 12024.772 | 149.825
0.685 | 12071.821 | 153.566
0.69 | 12212.968 | 152.781
0.695 | 12495.262 | 147.112
0.7 | 12401.164 | 146.783
0.705 | 11648.38 | 151.449
0.71 | 12024.772 | 153.57
0.715 | 12260.017 | 155.099
0.72 | 11554.281 | 152.86
0.725 | 12401.164 | 155.501
0.73 | 11695.429 | 148.64
0.735 | 12071.821 | 156.754
0.74 | 11883.625 | 154.475
0.745 | 11554.281 | 157.79
0.75 | 11836.576 | 157.898
0.755 | 11648.38 | 159.248
0.76 | 11742.478 | 159.985
0.765 | 11695.429 | 158.737
0.77 | 11930.674 | 157.12
0.775 | 12024.772 | 155.847
0.78 | 11130.84 | 161.28
0.785 | 11507.232 | 170.276
0.79 | 11507.232 | 171.966
0.795 | 11177.889 | 170.804
0.8 | 11366.085 | 167.867
0.805 | 11319.036 | 167.91
0.81 | 11601.331 | 165.996
0.815 | 11507.232 | 164.17
0.82 | 11648.38 | 162.462
0.825 | 11742.478 | 162.01
0.83 | 11648.38 | 159.702
0.835 | 11648.38 | 160.427
0.84 | 11177.889 | 158.612
0.845 | 11883.625 | 164.474
0.85 | 11648.38 | 158.639
0.855 | 11177.889 | 163.206
0.86 | 11507.232 | 166.832
0.865 | 11319.036 | 168.052
0.87 | 11271.987 | 168.23
0.875 | 11319.036 | 170.111
0.88 | 10613.301 | 175.177
0.885 | 10895.595 | 181.344
0.89 | 10754.448 | 183.961
0.895 | 10754.448 | 185.448
0.9 | 10848.546 | 183.648
0.905 | 10801.497 | 181.805
0.91 | 11177.889 | 178.93
0.915 | 11036.742 | 177.584
0.92 | 7938.007 | 177.163
0.925 | 10895.595 | 178.288
0.93 | 10895.595 | 179.453
0.935 | 11319.036 | 175.395
0.94 | 11366.085 | 170.197
0.945 | 11366.085 | 166.92
0.95 | 11319.036 | 166.503
0.955 | 11224.938 | 170.746
0.96 | 11083.791 | 172.036
0.965 | 11036.742 | 175.606
0.97 | 10801.497 | 176.513
0.975 | 10989.693 | 179.016
0.98 | 11036.742 | 175.26
0.985 | 11271.987 | 174.75
0.99 | 10989.693 | 172.478
0.995 | 10707.399 | 176.507
1 | 10707.399 | 178.456
1.005 | 10848.546 | 181.437
1.01 | 10895.595 | 181.896
1.015 | 10989.693 | 181.193
1.02 | 10754.448 | 180.577
1.025 | 10425.105 | 186.655
1.03 | 10895.595 | 191.117
1.035 | 11083.791 | 180.034
1.04 | 10848.546 | 179.75
1.045 | 10895.595 | 181.573
1.05 | 10519.203 | 183.119
1.055 | 10707.399 | 187.187
1.06 | 10895.595 | 185.358
1.065 | 10707.399 | 186.147
1.07 | 10754.448 | 184.367
1.075 | 10754.448 | 185.789
1.08 | 10472.154 | 186.392
1.085 | 10660.35 | 186.811
1.09 | 10942.644 | 186.371
1.095 | 10566.252 | 182.987
1.1 | 10707.399 | 188.636
1.105 | 10613.301 | 188.709
1.11 | 10519.203 | 190.917
1.115 | 10189.859 | 194.27
1.12 | 9954.614 | 198.825
1.125 | 10048.712 | 201.447
1.13 | 10001.663 | 202.508
1.135 | 10189.859 | 203.337
1.14 | 9766.418 | 203.555
1.145 | 10095.761 | 203.205
1.15 | 10189.859 | 202.957
1.155 | 10095.761 | 203.709
1.16 | 10048.712 | 203.888
1.165 | 9813.467 | 207.191
1.17 | 9766.418 | 209.382
1.175 | 9672.32 | 210.452
1.18 | 9954.614 | 209.423
1.185 | 10472.154 | 202.743
1.19 | 10095.761 | 198.19
1.195 | 10236.908 | 197.776
1.2 | 10048.712 | 197.497
1.205 | 10283.957 | 197.111
1.21 | 10425.105 | 195.733
1.215 | 10283.957 | 193.628
1.22 | 10566.252 | 190.216
1.225 | 10660.35 | 190.523
1.23 | 10236.908 | 191.166
1.235 | 10331.006 | 192.934
1.24 | 10095.761 | 195.084
1.245 | 10236.908 | 198.306
1.25 | 9954.614 | 198.927
1.255 | 10048.712 | 200.206
1.26 | 10001.663 | 200.23
1.265 | 10189.859 | 198.625
1.27 | 10425.105 | 197.507
1.275 | 9954.614 | 197.564
1.28 | 9813.467 | 203.857
1.285 | 8401.996 | 213.933
1.29 | 7461.015 | 235.506
1.295 | 10048.712 | 235.537
1.3 | 10189.859 | 213.579
1.305 | 9907.565 | 201.575
1.31 | 9766.418 | 210.696
1.315 | 9342.977 | 213.317
1.32 | 9578.222 | 214.149
1.325 | 7931.505 | 243.831
1.33 | 8543.143 | 274.785
1.335 | 9813.467 | 232.078
1.34 | 10095.761 | 201.661
1.345 | 10001.663 | 206.274
1.35 | 10189.859 | 201.739
1.355 | 10236.908 | 196.865
1.36 | 10048.712 | 202.81
1.365 | 9719.369 | 203.706
1.37 | 10048.712 | 207.103
1.375 | 10095.761 | 202.136
1.38 | 10048.712 | 196.753
1.385 | 10189.859 | 196.611
1.39 | 10001.663 | 196.442
1.395 | 9907.565 | 200.497
1.4 | 10048.712 | 201.699
1.405 | 9766.418 | 204.192
1.41 | 10048.712 | 203.855
1.415 | 9766.418 | 204.849
1.42 | 10001.663 | 204.032
1.425 | 9766.418 | 205.693
1.43 | 9719.369 | 207.401
1.435 | 9719.369 | 207.467
1.44 | 9060.682 | 216.366
1.445 | 9201.829 | 225.381
1.45 | 8872.486 | 226.195
1.455 | 6755.279 | 252.876
1.46 | 7884.456 | 313.274
1.465 | 8307.898 | 291.076
1.47 | 8872.486 | 247.28
1.475 | 8731.339 | 260.429
1.48 | 10142.81 | 238.308
1.485 | 10048.712 | 210.194
1.49 | 9907.565 | 201.867
1.495 | 10001.663 | 202.268
1.5 | 9860.516 | 205.339
1.505 | 9719.369 | 207.898
1.51 | 9672.32 | 208.191
1.515 | 9813.467 | 208.656
1.52 | 9766.418 | 208.122
1.525 | 9625.271 | 206.708
1.53 | 9719.369 | 208.299
1.535 | 9625.271 | 210.428
1.54 | 9531.173 | 210.564
1.545 | 9719.369 | 211.977
1.55 | 9484.124 | 212.798
1.555 | 9672.32 | 212.873
1.56 | 9060.682 | 215.681
1.565 | 9390.026 | 224.06
1.57 | 9248.879 | 228.234
1.575 | 8213.8 | 227.652
1.58 | 7743.309 | 235.949
1.585 | 8213.8 | 248.274
1.59 | 8590.192 | 280.784
1.595 | 9813.467 | 241.06
1.6 | 9531.173 | 204.835
1.605 | 9390.026 | 217.376
1.61 | 9437.075 | 215.884
1.615 | 9437.075 | 218.854
1.62 | 9390.026 | 218.406
1.625 | 9107.731 | 218.744
1.63 | 9625.271 | 222.967
1.635 | 9342.977 | 217.557
1.64 | 9437.075 | 216.083
1.645 | 9531.173 | 213.482
1.65 | 8449.045 | 237.594
1.655 | 9342.977 | 263.329
1.66 | 9013.633 | 222.86
1.665 | 6614.132 | 248.268
1.67 | 7743.309 | 326.38
1.675 | 8119.702 | 241.577
1.68 | 7366.917 | 221.967
1.685 | 9342.977 | 252.542
1.69 | 9342.977 | 222.362
1.695 | 9248.879 | 223.392
1.7 | 9201.829 | 222.513
1.705 | 9578.222 | 221.014
1.71 | 9295.928 | 218.044
1.715 | 9390.026 | 220.744
1.72 | 9531.173 | 216.423
1.725 | 9625.271 | 210.674
1.73 | 9813.467 | 210.435
1.735 | 9154.78 | 212.919
1.74 | 9154.78 | 218.959
1.745 | 9342.977 | 224.457
1.75 | 8825.437 | 225.827
1.755 | 9248.879 | 224.41
1.76 | 9201.829 | 224.201
1.765 | 9201.829 | 223.829
1.77 | 9107.731 | 225.411
1.775 | 8731.339 | 230.529
1.78 | 8543.143 | 234.581
1.785 | 8166.751 | 240.267
1.79 | 8543.143 | 236.441
1.795 | 8401.996 | 281.995
1.8 | 5720.2 | 331.529
1.805 | 6990.525 | 321.369
1.81 | 7084.623 | 284.72
1.815 | 8354.947 | 272.156
1.82 | 6708.23 | 248.947
1.825 | 8213.8 | 312.818
1.83 | 7555.113 | 295.382
1.835 | 8731.339 | 267.778
1.84 | 9107.731 | 243.128
1.845 | 9295.928 | 219.829
1.85 | 9013.633 | 226.771
1.855 | 9060.682 | 227.261
1.86 | 8966.584 | 230.204
1.865 | 8825.437 | 230.884
1.87 | 8919.535 | 229.89
1.875 | 8919.535 | 232.419
1.88 | 8778.388 | 232.11
1.885 | 8778.388 | 231.762
1.89 | 9107.731 | 231.2
1.895 | 8166.751 | 240.151
1.9 | 8354.947 | 250.014
1.905 | 7743.309 | 260.149
1.91 | 6096.593 | 288.194
1.915 | 5437.906 | 329.006
1.92 | 6496.51 | 339.721
1.925 | 8401.996 | 295.251
1.93 | 8496.094 | 251.043
1.935 | 8966.584 | 239.923
1.94 | 8778.388 | 234.401
1.945 | 8778.388 | 235.177
1.95 | 8637.241 | 235.895
1.955 | 7225.77 | 263.284
1.96 | 6237.74 | 295.707
1.965 | 6896.426 | 317.744
1.97 | 7508.064 | 289.381
1.975 | 5720.2 | 295.302
1.98 | 6331.838 | 331.477
1.985 | 8213.8 | 294.125
1.99 | 9060.682 | 255.89
1.995 | 8684.29 | 228.563
2 | 8825.437 | 231.107
2.005 | 9013.633 | 233.732
2.01 | 7366.917 | 263.365
2.015 | 7272.819 | 294.829
2.02 | 8401.996 | 290.573
2.025 | 8637.241 | 261.092
2.03 | 8825.437 | 237.961
2.035 | 9013.633 | 231.387
2.04 | 8872.486 | 229.607
2.045 | 8872.486 | 227.75
2.05 | 8825.437 | 228.633
2.055 | 8778.388 | 229.446
2.06 | 8684.29 | 224.714
2.065 | 7272.819 | 261.112
2.07 | 7413.966 | 301.764
2.075 | 8872.486 | 240.682
2.08 | 9013.633 | 227.254
2.085 | 8919.535 | 223.171
2.09 | 9013.633 | 226.282
2.095 | 8401.996 | 229.317
2.1 | 8449.045 | 236.747
2.105 | 8354.947 | 244.421
2.11 | 10095.761 | 242.429
2.115 | 10604.49 | 194.473

## Test-7281
Report number | K-352123-001- R00
Prepared for | Hydro Québec
Issue Date | 2019-January-25
Citation | K. Gray, S. Robert and T. L. Gauthier, "Low Voltage 100–500 Vdc Arc Flash Testing," 2020 IEEE IAS Electrical Safety Workshop (ESW), Reno, NV, USA, 2020, pp. 1-7, doi: 10.1109/ESW42757.2020.9188336.
Test Number | 7281
Scenario | 500 V - 20 kA Available - 6mm gap, ceramic box, calorimeters at 18"
Test Voltage (V) | 518.7
Arc Current (A) | 10990
Arc Voltage (V) | 180.8
Duration of Arc (s) | 2.004
Arc Energy (kJ) | 3725
Incident Energy at 450 mm Distance (cal/cm²) | 44.6
Electrode Gap (mm) | 6
Final Electrode Gap (mm) | 130
Configuration | inline
Time (s) | Current (A) | Voltage (V) | I | Vbat
0.115 | 8847.438 | 65.651 | 0 | 520
0.12 | 13582.068 | 65.999 | 20000 | 0
0.125 | 15434.749 | 62.773
0.13 | 15482.254 | 62.138
0.135 | 15909.796 | 61.364
0.14 | 15862.291 | 59.272
0.145 | 15672.272 | 57.422
0.15 | 15814.786 | 54.997
0.155 | 15814.786 | 53.021
0.16 | 16052.309 | 52.888
0.165 | 16052.309 | 54.307
0.17 | 16052.309 | 56.639
0.175 | 16147.319 | 58.739
0.18 | 15767.282 | 59.994
0.185 | 15719.777 | 61.303
0.19 | 15814.786 | 62.063
0.195 | 15577.263 | 62.94
0.2 | 15767.282 | 64.253
0.205 | 15434.749 | 65.774
0.21 | 15767.282 | 67.253
0.215 | 15624.768 | 69.402
0.22 | 15387.244 | 71.659
0.225 | 15529.758 | 73.137
0.23 | 15149.721 | 74.79
0.235 | 15197.226 | 77.116
0.24 | 15054.712 | 78.836
0.245 | 15007.207 | 79.867
0.25 | 15054.712 | 80.483
0.255 | 14674.675 | 80.054
0.26 | 14912.198 | 79.045
0.265 | 15054.712 | 79.836
0.27 | 14912.198 | 81.398
0.275 | 15149.721 | 83.262
0.28 | 14674.675 | 85.273
0.285 | 14912.198 | 86.921
0.29 | 14769.684 | 88.19
0.295 | 14484.656 | 89.491
0.3 | 14769.684 | 90.828
0.305 | 14437.151 | 92.282
0.31 | 14484.656 | 94.555
0.315 | 14294.637 | 97.011
0.32 | 14294.637 | 99.192
0.325 | 14294.637 | 101.147
0.33 | 13914.6 | 101.163
0.335 | 14199.628 | 100.598
0.34 | 14199.628 | 99.73
0.345 | 14057.114 | 99.51
0.35 | 14294.637 | 100.683
0.355 | 14009.61 | 101.016
0.36 | 14437.151 | 101.393
0.365 | 13867.096 | 103.061
0.37 | 14057.114 | 102.912
0.375 | 14152.124 | 102.987
0.38 | 13914.6 | 104.85
0.385 | 13867.096 | 106.345
0.39 | 13914.6 | 108.245
0.395 | 13724.582 | 112.786
0.4 | 13772.086 | 116.117
0.405 | 13534.563 | 119.867
0.41 | 13629.572 | 122.957
0.415 | 13344.545 | 124.441
0.42 | 13154.526 | 124.133
0.425 | 13297.04 | 122.631
0.43 | 13107.021 | 122.082
0.435 | 13392.049 | 120.625
0.44 | 13344.545 | 118.817
0.445 | 13202.031 | 119.417
0.45 | 13392.049 | 118.67
0.455 | 13344.545 | 117.756
0.46 | 13534.563 | 119.068
0.465 | 13154.526 | 120.343
0.47 | 13297.04 | 120.954
0.475 | 13392.049 | 121.999
0.48 | 13154.526 | 121.989
0.485 | 13344.545 | 121.466
0.49 | 13297.04 | 120.472
0.495 | 13249.535 | 120.658
0.5 | 13297.04 | 121.43
0.505 | 13297.04 | 122.771
0.51 | 13249.535 | 123.437
0.515 | 12917.003 | 122.957
0.52 | 12964.507 | 124.622
0.525 | 13154.526 | 126.46
0.53 | 13107.021 | 129.238
0.535 | 13154.526 | 133.59
0.54 | 12821.993 | 139.793
0.545 | 12964.507 | 144.735
0.55 | 12489.461 | 144.429
0.555 | 12156.928 | 143.005
0.56 | 12346.947 | 138.318
0.565 | 12299.442 | 130.565
0.57 | 12489.461 | 124.033
0.575 | 12821.993 | 122.08
0.58 | 13012.012 | 122.953
0.585 | 13249.535 | 127.169
0.59 | 12917.003 | 130.802
0.595 | 12726.984 | 132.945
0.6 | 12584.47 | 135.266
0.605 | 12726.984 | 134.687
0.61 | 12917.003 | 137.291
0.615 | 12394.452 | 139.054
0.62 | 12774.489 | 139.994
0.625 | 12394.452 | 142.45
0.63 | 12394.452 | 142.711
0.635 | 12631.975 | 144.188
0.64 | 12061.919 | 143.969
0.645 | 12251.938 | 142.048
0.65 | 12204.433 | 139.975
0.655 | 12299.442 | 142.143
0.66 | 12774.489 | 143.566
0.665 | 12109.424 | 147.089
0.67 | 12441.956 | 150.917
0.675 | 12204.433 | 156.004
0.68 | 12061.919 | 160.483
0.685 | 11824.396 | 163.136
0.69 | 11539.368 | 154.97
0.695 | 11776.891 | 162.467
0.7 | 11966.91 | 161.134
0.705 | 11634.377 | 162.767
0.71 | 11491.863 | 161.274
0.715 | 11539.368 | 157.77
0.72 | 11634.377 | 157.651
0.725 | 11681.882 | 151.587
0.73 | 11634.377 | 157.591
0.735 | 12061.919 | 157.779
0.74 | 11254.34 | 158.31
0.745 | 11824.396 | 155.587
0.75 | 11871.9 | 155.166
0.755 | 11586.873 | 156.411
0.76 | 12109.424 | 157.602
0.765 | 11681.882 | 159.153
0.77 | 11634.377 | 162.377
0.775 | 11539.368 | 161.585
0.78 | 11586.873 | 161.089
0.785 | 11301.845 | 158.518
0.79 | 11491.863 | 156.167
0.795 | 11871.9 | 155.467
0.8 | 11586.873 | 156.669
0.805 | 11871.9 | 158.525
0.81 | 11586.873 | 162.22
0.815 | 11634.377 | 164.825
0.82 | 11539.368 | 165.623
0.825 | 11396.854 | 166.442
0.83 | 11206.835 | 165.532
0.835 | 11539.368 | 164.815
0.84 | 11206.835 | 162.409
0.845 | 11586.873 | 161.46
0.85 | 11159.331 | 159.484
0.855 | 11634.377 | 158.474
0.86 | 11634.377 | 158.968
0.865 | 11396.854 | 160.519
0.87 | 11634.377 | 161.549
0.875 | 11491.863 | 162.677
0.88 | 11491.863 | 165.317
0.885 | 11301.845 | 166.495
0.89 | 11539.368 | 168.523
0.895 | 11206.835 | 177.153
0.9 | 11159.331 | 170.339
0.905 | 10731.789 | 165.502
0.91 | 11064.321 | 166.627
0.915 | 11539.368 | 168.804
0.92 | 11349.349 | 171.186
0.925 | 10969.312 | 171.894
0.93 | 10921.808 | 171.064
0.935 | 11206.835 | 168.534
0.94 | 10969.312 | 168.103
0.945 | 11301.845 | 164.203
0.95 | 11301.845 | 163.132
0.955 | 11206.835 | 161.635
0.96 | 11634.377 | 170.901
0.965 | 11634.377 | 176.021
0.97 | 11016.817 | 180.205
0.975 | 10494.266 | 176.57
0.98 | 11111.826 | 175.814
0.985 | 10874.303 | 180.099
0.99 | 10969.312 | 184.457
0.995 | 10636.78 | 181.589
1 | 10589.275 | 178.102
1.005 | 10969.312 | 174.618
1.01 | 11016.817 | 171.713
1.015 | 11254.34 | 169.823
1.02 | 10969.312 | 168.949
1.025 | 10874.303 | 169.254
1.03 | 11159.331 | 170.649
1.035 | 11064.321 | 177.536
1.04 | 10636.78 | 172.29
1.045 | 10874.303 | 170.025
1.05 | 11064.321 | 177.037
1.055 | 11016.817 | 171.861
1.06 | 10921.808 | 170.805
1.065 | 11159.331 | 171.87
1.07 | 11206.835 | 174.057
1.075 | 10921.808 | 176.216
1.08 | 10969.312 | 180.965
1.085 | 11064.321 | 187.737
1.09 | 10446.761 | 191.478
1.095 | 10731.789 | 182.323
1.1 | 10066.724 | 178.669
1.105 | 10921.808 | 177.965
1.11 | 10874.303 | 179.833
1.115 | 10731.789 | 187.039
1.12 | 10826.798 | 195.808
1.125 | 10066.724 | 196.989
1.13 | 10209.238 | 190.424
1.135 | 10114.229 | 183.101
1.14 | 10636.78 | 185.15
1.145 | 10494.266 | 187.794
1.15 | 10351.752 | 189.426
1.155 | 10446.761 | 190.691
1.16 | 10161.733 | 191.392
1.165 | 10114.229 | 189.205
1.17 | 10304.247 | 184.204
1.175 | 10066.724 | 179.095
1.18 | 10779.294 | 178.762
1.185 | 10731.789 | 176.297
1.19 | 10494.266 | 175.874
1.195 | 10731.789 | 176.341
1.2 | 10636.78 | 178.209
1.205 | 10969.312 | 179.868
1.21 | 10541.77 | 183.77
1.215 | 10304.247 | 176.37
1.22 | 10494.266 | 173.06
1.225 | 10684.284 | 183.814
1.23 | 11016.817 | 195.927
1.235 | 10209.238 | 206.708
1.24 | 9496.668 | 203.08
1.245 | 9781.696 | 201.244
1.25 | 9734.191 | 195.334
1.255 | 9829.201 | 190.645
1.26 | 10209.238 | 187.024
1.265 | 10351.752 | 186.249
1.27 | 10446.761 | 185.878
1.275 | 10351.752 | 189.034
1.28 | 10636.78 | 188.849
1.285 | 10161.733 | 190.514
1.29 | 10256.742 | 191.152
1.295 | 10446.761 | 197.014
1.3 | 10161.733 | 202.439
1.305 | 9829.201 | 205.815
1.31 | 9686.687 | 207.324
1.315 | 9496.668 | 230.234
1.32 | 9544.173 | 268.713
1.325 | 8451.566 | 261.529
1.33 | 7691.491 | 220.722
1.335 | 9449.163 | 197.554
1.34 | 10209.238 | 206.834
1.345 | 9829.201 | 215.902
1.35 | 9354.154 | 219.555
1.355 | 9686.687 | 221.472
1.36 | 9164.136 | 244.008
1.365 | 8879.108 | 252.035
1.37 | 7738.996 | 222.709
1.375 | 9211.64 | 209.8
1.38 | 9781.696 | 210.42
1.385 | 9449.163 | 209.95
1.39 | 9449.163 | 211.963
1.395 | 9496.668 | 211.802
1.4 | 9639.182 | 208.454
1.405 | 9496.668 | 236.938
1.41 | 9354.154 | 275.642
1.415 | 8546.575 | 260.568
1.42 | 7501.473 | 217.394
1.425 | 9069.126 | 200.487
1.43 | 9876.705 | 199.561
1.435 | 9639.182 | 199.794
1.44 | 9876.705 | 198.761
1.445 | 9971.715 | 197.928
1.45 | 9734.191 | 200.664
1.455 | 9829.201 | 201.465
1.46 | 9781.696 | 199.491
1.465 | 9734.191 | 196.833
1.47 | 10114.229 | 200.123
1.475 | 9829.201 | 201.852
1.48 | 9924.21 | 203.379
1.485 | 9591.677 | 205.113
1.49 | 9639.182 | 205.206
1.495 | 9591.677 | 205.801
1.5 | 9449.163 | 207.366
1.505 | 9734.191 | 208.736
1.51 | 9449.163 | 210.711
1.515 | 9639.182 | 211.103
1.52 | 9496.668 | 207.194
1.525 | 9354.154 | 205.354
1.53 | 9591.677 | 198.868
1.535 | 9924.21 | 207.275
1.54 | 9639.182 | 204.261
1.545 | 9639.182 | 208.043
1.55 | 9449.163 | 210.934
1.555 | 9639.182 | 216.038
1.56 | 9496.668 | 220.014
1.565 | 9164.136 | 222.516
1.57 | 8879.108 | 228.397
1.575 | 9211.64 | 241.259
1.58 | 7786.501 | 233.753
1.585 | 7216.445 | 211.068
1.59 | 8926.612 | 198.834
1.595 | 9639.182 | 198.176
1.6 | 9876.705 | 198.802
1.605 | 10066.724 | 202.024
1.61 | 9829.201 | 206.458
1.615 | 9591.677 | 212.761
1.62 | 9496.668 | 213.412
1.625 | 9449.163 | 219.604
1.63 | 9069.126 | 226.139
1.635 | 9259.145 | 242.439
1.64 | 8689.089 | 247.986
1.645 | 7786.501 | 217.087
1.65 | 9164.136 | 211.709
1.655 | 9401.659 | 211.082
1.66 | 9449.163 | 211.182
1.665 | 9449.163 | 213.177
1.67 | 9306.65 | 213.015
1.675 | 9354.154 | 213.209
1.68 | 9259.145 | 211.492
1.685 | 9306.65 | 207.764
1.69 | 9496.668 | 206.241
1.695 | 9401.659 | 203.467
1.7 | 9686.687 | 212.281
1.705 | 9591.677 | 225.301
1.71 | 8831.603 | 220.991
1.715 | 9306.65 | 221.397
1.72 | 8974.117 | 233.998
1.725 | 8926.612 | 229.92
1.73 | 8926.612 | 228.401
1.735 | 8451.566 | 227.866
1.74 | 8879.108 | 235.757
1.745 | 8831.603 | 313.537
1.75 | 7192.693 | 249.859
1.755 | 7311.454 | 211.973
1.76 | 9021.622 | 218.315
1.765 | 9021.622 | 217.556
1.77 | 9211.64 | 215.719
1.775 | 8974.117 | 214.957
1.78 | 9164.136 | 216.967
1.785 | 9354.154 | 220.14
1.79 | 9069.126 | 223.607
1.795 | 8784.098 | 224.036
1.8 | 8831.603 | 223.386
1.805 | 8974.117 | 222.842
1.81 | 8926.612 | 221.956
1.815 | 9116.631 | 227.643
1.82 | 9021.622 | 242.779
1.825 | 8879.108 | 272.418
1.83 | 7691.491 | 271.425
1.835 | 6978.922 | 242.89
1.84 | 8214.043 | 276.073
1.845 | 8071.529 | 255.158
1.85 | 6646.389 | 230.588
1.855 | 8261.547 | 211.704
1.86 | 9259.145 | 219.973
1.865 | 9354.154 | 242.639
1.87 | 8499.07 | 233.032
1.875 | 8404.061 | 250.073
1.88 | 8261.547 | 249.04
1.885 | 7738.996 | 234.371
1.89 | 8404.061 | 241.42
1.895 | 8546.575 | 247.918
1.9 | 8071.529 | 250.889
1.905 | 7834.005 | 271.524
1.91 | 8024.024 | 294.972
1.915 | 7216.445 | 302.696
1.92 | 6693.894 | 301.228
1.925 | 7691.491 | 276.824
1.93 | 6598.885 | 259.673
1.935 | 7548.978 | 253.85
1.94 | 7834.005 | 249.697
1.945 | 8309.052 | 244.903
1.95 | 8119.033 | 233.397
1.955 | 8119.033 | 228.14
1.96 | 8784.098 | 227.251
1.965 | 8831.603 | 230.591
1.97 | 8546.575 | 223.148
1.975 | 8546.575 | 224.99
1.98 | 8926.612 | 229.487
1.985 | 8831.603 | 232.755
1.99 | 8499.07 | 236.082
1.995 | 8546.575 | 237.732
2 | 8356.557 | 239.314
2.005 | 8309.052 | 251.49
2.01 | 8356.557 | 261.383
2.015 | 7453.968 | 245.824
2.02 | 7976.519 | 247.248
2.025 | 8309.052 | 245.799
2.03 | 8214.043 | 262.45
2.035 | 8214.043 | 306.388
2.04 | 8024.024 | 359.126
2.045 | 3843.615 | 312.538
2.05 | 5126.241 | 269.438
2.055 | 7311.454 | 242.893
2.06 | 8214.043 | 235.271
2.065 | 8404.061 | 233.309
2.07 | 8499.07 | 228.583
2.075 | 8784.098 | 240.803
2.08 | 8499.07 | 267.086
2.085 | 8119.033 | 296.101
2.09 | 6551.38 | 316.877
2.095 | 5648.792 | 277.138
2.1 | 6408.866 | 248.105
2.105 | 8071.529 | 235.821
2.11 | 8546.575 | 239.684
2.115 | 8404.061 | 196.673
2.12 | 8451.566 | 173.653
2.125 | 8641.585 | 231.731